PSS0 Maintenance Plan

|  | Name | Role/Title |
| --- | --- | --- |
| Owner | Stuart Birch | Senior Engineer |
| Author | Mattias Eriksson | Technician- Protection Systems |
| Reviewer | Morteza Mansouri | Lead Integrator Engineer |
| Approver | Annika Nordt | Group Leader - Protection Systems |

| Table of content | Page |
| --- | --- |

1.	introduction	4

1.1	Purpose of the document	4

1.1.	Roles and responsibilities	5

1.2.	PSS0 overview	5

2.	Preparation before maintenance	6

2.1.	Equipment involved	6

2.2.	Requirements	7

2.3.	Safety	7

2.4.	Consumables	8

2.5.	Preliminary checks	8

3.	Preventive maintenance	8

4.	Breakdown maintenance	8

5.	Proof Test	9

6.	Equipment	10

6.1.1.	Acc-Z0:PSS-ACB-1 Field box containing the Exchange Key Switch	10

6.1.2.	Acc-Z0:PSS-Ann-1 Signal Column (Green light + sounder)	11

6.1.3.	Acc-Z0:PSS-ESB-1 Emergency Stop Button	11

6.1.4.	Acc-Z0:PSS-GRly-1 HV Grounding Relay	12

6.1.5.	Acc-Z0:PSS-GRod-1 HV Grounding Rod	13

6.1.6.	Acc-Z0:PSS-LiP-1 HV ON Light Panel	14

Acc-Z0:PSS-LiP-2	
Beam ON Light Panel 2 off	14

6.1.7.	Acc-Z0:PSS-MeL-1	15

6.1.8.	Acc-Z0:PSS-MeS-1 Mechanical Safety Switch	16

6.1.9.	Acc-Z0:PSS-MgS-1 Magnetic Safety Switch	16

6.1.10.	Acc-Z0:PSS-RIO-1 Sub-Rack for Remote I/O inside ISrc HV fenced area (Red Sys.)	17

Acc-Z0:PSS-RIO-2	Sub-Rack for Remote I/O inside ISrc HV fenced area (Blue Sys.)	17

6.1.11.	Acc-Z0:PSS-SeB-1 Illuminated Search Button inside ISrc HV fenced area	18

6.1.12.	Acc-Z0:PSS-LiP-1 HV ON Light Panel Acc-Z0:PSS-LiP-2 Beam ON Light Panel ACC-Z0:PSS-LiP-3    Beam ON Light Panel	19

6.1.13.	FEB-010Row: CnPw-U-001  PSS Red Sys. PLC Rack	20

6.1.14.	FEB-010Row: CnPw-U-007  PSS HV PS Contactors Rack	20

7.	Abbreviations	21

8.	References	22

9.	Document Revision history	22

list of tables

Tabell 1 PSS0 Field devices	6

Tabell 2 Consumables	8

list of Figures

Figur 1 Key exchange box	10

Figur 2 Signal column	11

Figur 3 Emergency stop button	12

Figur 4 Grounding relay	13

Figur 5 Grouding red	14

Figur 6 Key exchange lock	16

Figur 7 Mechanical safety switch	17

Figur 8 Magnetic safety switch	18

Figur 9 Search button	19

# introduction

## Purpose of the document

This document provides a maintenance manual for the Accelerator Personnel Safety System 0 (PSS0) at European Spallation Source ERIC in Lund, Sweden. The objective is to describe how to preform maintenance for PSS0.

When performing maintenance, the forms in Appendix 1 are to be used. Documentation and reports shall be uploaded to CHESS after maintenance is carried out.

## Roles and responsibilities

The protection and safety systems group within ICS shall carry out and plan both preventive and breakdown maintenance for PSS0.

The PLC application programmer shall take part in the planning and preparation of the maintenance.

Shift leader (or equivalent, according to Operations) shall confirm and approve the maintenance plan according to. [1]

## PSS0 overview

PSS0 overview can be found in [2] Concept of Operations for the Accelerator Personnel Safety System 0 (PSS0), Hardware Design specifications can be found in [3].

# Preparation before maintenance

## Equipment involved

Table 1: PSS0 Field devices

| ESS name |  | Device function | Preventive maintenance | Proof testing Interval |
| --- | --- | --- | --- | --- |
| Acc-Z0:PSS-ACB-1 | Field box containing the Exchange Key Switch | Every 12 months | Every 2 years |
| Acc-Z0:PSS-Ann-1 | Signal Column (Green light + sounder) | Every 12 months | Every 2 years |
| Acc-Z0:PSS-ESB-1 | Emergency Stop Button | Every 12 months | Every 2 years |
| Acc-Z0:PSS-GRly-1 | HV Grounding Relay | Every 12 months | Every 2 years |
| Acc-Z0:PSS-GRod-1 | HV Grounding Rod | Every 12 months | Every 2 years |
| Acc-Z0:PSS-LiP-1 | HV ON Light Panel | Every 12 months | Every 2 years |
| Acc-Z0:PSS-LiP-2 | Beam ON Light Panel | Every 12 months | Every 2 years |
| ACC-Z0:PSS-LiP-3 | Beam ON Light Panel | Every 12 months | Every 2 years |
| Acc-Z0:PSS-MeL-1 | Mechanical Lock | Every 12 months | Every 2 years |
| Acc-Z0:PSS-MeS-1 | Mechanical Safety Switch | Every 12 months | Every 2 years |
| Acc-Z0:PSS-MgS-1 | Magnetic Safety Switch | Every 12 months | Every 2 years |
| Acc-Z0:PSS-RIO-1 | Sub-Rack for Remote I/O inside ISrc HV fenced area (Red Sys.) | Every 12 months | Every 2 years |
| Acc-Z0:PSS-RIO-2 | Sub-Rack for Remote I/O inside ISrc HV fenced area (Blue Sys.) | Every 12 months | Every 2 years |
| Acc-Z0:PSS-SeB-1 | Illuminated Search Button inside ISrc HV fenced area | Every 12 months | Every 2 years |
| Acc-Z0:PSS-SeB-2 | Illuminated Search Button inside ISrc HV fenced area | Every 12 months | Every 2 years |
| FEB-010Row: CnPw-U-001 | PSS Red Sys. PLC Rack | Every 12 months | Every 2 years |
| FEB-010Row: CnPw-U-002 | PSS Red Sys. Remote IO Rack | Every 12 months | Every 2 years |
| FEB-010Row: CnPw-U-007 | PSS HV PS Contactors Rack | Every 12 months | Every 2 years |
| FEB-020Row: CnPw-U-009 | PSS Blue Sys. PLC Rack | Every 12 months | Every 2 years |
| FEB-020Row: CnPw-U-0010 | PSS Blue Sys. Remote IO Rack | Every 12 months | Every 2 years |

## Requirements

To ensure the reliability of the PSS0 system, all field devices and PSS0 racks (U1-U9) need to be maintained properly. Focus shall be on the mechanical and electrical components.

All hardware is fully detailed in [3].

A list of spare parts, special tools/measure equipment that are needed for maintenance are detailed in table 2.

UPS batteries are to be checked prior to maintenance according to the manual [4], and if needed replaced. 
This procedure is done according to the manual for the specific UPS.

## Safety

- Personal protection equipment (PPE) according to ESS regulations are to be worn at all time. Required documentation and permits shall be filled in according to ESS rules. These shall include risk assessments and work orders.

- Personnel taking part in the maintenance needs to be trained according to ESS regulations.

- All equipment used for measurement needs to be calibrated.

- Lock-Out/Tag-Out (LOTO) shall be in place before electrical work and maintenance is preformed according to ESS LOTO procedures [5]

- Consumables (such as filters) and tools shall be handled according to ESS regulations.

- PSS0 PLC equipment and field devices are powered by 24VDC UPS power; this has to be taken in to consideration when preforming maintenance.

- When replacing UPS batteries special attention have to be taken to ensure safety when handling the batteries.

## Consumables

Table 2 lists the consumables needed to perform preventive maintenance.

Table 2: Consumables

| Name | Quantity | Manufacturer/number | Note |
| --- | --- | --- | --- |
| Filter for racks | 10 | Shroff |  |
| Multi USE lubrication | 1 | Any penetrating water displacing lubrication |  |
| LED light for search button | 2 | SIE.3SB3901-1DA |  |
| LED light for light Colum | 1 | SIE.3SB3901-1DA |  |
| LED light for Emergency stop button | 1 | SIE.3SU1401-1BB00-1AA0 |  |

## Preliminary checks

Before carrying out maintenance, it is important to verify and document the current system status. Checking system logs and protocols from the last performed proof test protocol shall be carried out.

# Preventive maintenance

Preventive maintenance according to Appendix 1 shall be performed to ensure that consumables and wear parts are replaced. Before replacing a component, the spare parts should be checked to be according to the previous installed versions in [6]. In case of end of life (EOL) for the spare parts, the PSS team needs to be contacted to assess the replacement part and update the documentation.

After final validation, preventive maintenance shall be carried out by the PSS team according to Table 1.

# Breakdown maintenance

Reported breakdown maintenance shall be checked and planned prior to preforming the maintenance together with the shift leader The work carried out should be documented and reported back to the shift leader according applicable Operations procedure. The PSS configuration management plan [7] is used for traceability.

# Proof Test

Proof testing shall be carried out according to [Table 1] and to be performed according to [8].

# Equipment

### Acc-Z0:PSS-ACB-1	Field box containing the Exchange Key Switch

#### Description

A box containing the key exchange for PSS0

Key exchange delivered by Fortress, part number according to [6].
Hardware requirements are according to [3].
Spare key for the key exchange is handled according to [9]

Figure 1 Key exchange box

#### Maintenance

Mechanical
- Check the mechanical function of the lock
- Visual inspection of mounting and installation.
- If required, use lubrication according to manufacture.
- Condition of box
- Remove dust and debris from box

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- In case one of the keys of key exchange system is missing, it shall be handled according to description in [9]

### Acc-Z0:PSS-Ann-1	Signal Column (Green light + sounder)

#### Description

Signal column with green light and sounder to indicate ongoing search

Hardware requirements are according to [6].

Figure 2 Signal column

#### Maintenance

Mechanical
- Visual inspection of mounting and installation.

Electrical
- Check the function of the light and sounder.
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
-For spare parts consult PSS0 Hardware Design Requirements Specifications [6].

### Acc-Z0:PSS-ESB-1	Emergency Stop Button

#### Description

Emergency stop button to cut the power supply to the HV platform.

Hardware requirements are according to [3].

Figure 3 Emergency stop button

#### Maintenance

Mechanical
- Visual inspection of mounting and installation.
- Check mushroom function, reset and hold.

Electrical
- Check illumination of button.
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
-For spare parts consult PSS0 Hardware Design Requirements Specifications [6].

### Acc-Z0:PSS-GRly-1	HV Grounding Relay

#### Description

Grounding relay for HV, to ensure that no HV can get through.

Hardware requirements are according to [3].

Figure 4 Grounding relay

#### Maintenance

Mechanical
- Visual inspection plexiglass cage for damage
- Remove plexiglass cage to inspect relay for mechanical damage
- Check mounting of the relay and mechanical function
- Lubrication
- Check state of HV contacts
- Clean dust out of relay and plexiglass cage
- Check terminations

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)
- Check torque markings on the grounding cable attached to the grounding bar.

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-GRod-1	HV Grounding Rod

#### Description

Grounding rod for HV cage. Connects to the cage via a hook on the left hand side. Has a parking switch that is actuated when the rod in in parking mode across the HV fence door.

Hardware requirements are according to [3].

Figure 5 Grounding rod

#### Maintenance

Mechanical
- Visual inspection of rod
- Visual inspection of cable attachments to rod
- Check parking switch mounting
- Check HV platform mounting
- Check connection details on the HV cage
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Electrical
- Ensure PE connectivity
- Check terminations
- Check torque markings on the grounding cable attached to the grounding bar.

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-LiP-1	HV ON Light Panel

### Acc-Z0:PSS-LiP-2	Beam ON Light Panel 2 off

#### Description

Light panels to indicate state of operation.

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-MeL-1

Figure 6 Key exchange lock

#### Description

Mechanical lock for ISrc HV fence access door

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting and installation.
- Visual inspection of mechanical function, in locked and unlocked mode.
- Functional testing of emergency escape function and reset.
- Lubrication of lock to ensure it runs smoothly.
- Inspect bracket for damage.
- Check torque markings on bolts that hold the lock

Electrical
- Ensure PE connectivity.

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-MeS-1	Mechanical Safety Switch

Figure 7 Mechanical safety switch

#### Description

Mechanical safety Switch for ISrc door, mounted on the inside of the door

Hardware requirements are according to [6].

#### Maintenance

Mechanical
- Visual inspection of mounting
- Visual inspection of mechanical function, in locked and unlocked mode
- Lubrication if needed

Electrical
- Check LED´s feedback
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-MgS-1	Magnetic Safety Switch

Figure 8 Magnetic safety switch

#### Description

Magnetic Safety switch for ISrc HV fence access door, mounted on the inside of the door.

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting
- Visual inspection of clearance when the door is closed min 3mm max 7mm

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-RIO-1	Sub-Rack for Remote I/O inside ISrc HV fenced area (Red Sys.)

### Acc-Z0:PSS-RIO-2	Sub-Rack for Remote I/O inside ISrc HV fenced area (Blue Sys.)

#### Description

Two sub racks in one 19“ 9U high containment in one of the racks on  the HV platform

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting and condition of the rack
- Clean the inside of the rack if needed

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-SeB-1	Illuminated Search Button inside ISrc HV fenced area

#### Acc-Z0:PSS-SeB-2	Illuminated Search Button inside ISrc HV fenced area

#### Description

Search buttons for ISrc HV cage.

Figure 9 Search button

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting
- Visual inspection of markings
- Visual inspection of lights in the LED

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### Acc-Z0:PSS-LiP-1	HV ON Light Panel
Acc-Z0:PSS-LiP-2	Beam ON Light Panel
ACC-Z0:PSS-LiP-3    Beam ON Light Panel

#### Description

Signs to indicate HV and Beam ON

Figure 10 Beam and HV ON panels

Hardware PSS0 Hardware Design Requirements Specifications are according to [3].

#### Maintenance

Mechanical
- Visual inspection of mounting
- Visual inspection of markings
- Visual inspection and cleaning of signs

Electrical
- Ensure PE connectivity
- Check terminations (it shall be done during ISrc and LEBT shutdown)

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### FEB-010Row: CnPw-U-001 	PSS Red Sys. PLC Rack

#### FEB-010Row: CnPw-U-002 	PSS Red Sys. Remote IO Rack

#### FEB-020Row: CnPw-U-003 	PSS Blue Sys. PLC Rack

#### FEB-020Row: CnPw-U-004 	PSS Blue Sys. Remote IO Rack

#### Description

PLC and RIO racks for PSS0

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of markings
- Visual inspection of overall mounting.
- Visual inspection of cabinet.
- Lubrication of door hinges and locks.
- Clean the inside of the rack if needed.
- Functional checks of HMI where present.
- filters

Electrical
- Electrical checks according to appendix, as reference [6]
- UPS status and battery date, needs to be replace every 4 years.
- UPS Status and condition can be checked using the PSS laptop and access the webserver connection in the UPS.
- Ensure PE connectivity.

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

### FEB-010Row: CnPw-U-007 	PSS HV PS Contactors Rack

#### Description

HV PS contactor rack that contains the power feed (400VAC contactor) for ISrc power supply.

Hardware requirements are according to [3].

#### Maintenance

Mechanical
- Visual inspection of markings
- Visual inspection of overall mounting.
- Visual inspection of cabinet.
- Lubrication of door hinges and locks.
- Clean the inside of the rack if needed.
- Functional checks of HMI where present.
- Filters

Electrical
- Electrical checks according to appendix, as reference [6]
- Ensure PE connectivity.

Spare parts
- For spare parts consult Accelerator PSS0 Electrical Circuit Diagram [6].

# Abbreviations

Abbreviation		Explanation

EOL			End of Life

FEB			Front End Building

G01			Accelerator Tunnel Building

HMI			Human Machine Interface

HV			High Voltage

HV PS			High Voltage Power Supply

ISrc			Ion Source

LOTO			Lock-Out/Tag-Out

MCB			Miniature Circuit Breaker

PE			Protective Earth

PLC			Programmable Logic Controller

PSS			Personnel Safety Systems

PSS0			Personnel Safety System for ISrc and LEBT Test Stand

UPS			Uninterruptible Power Supply

V			Voltage
VDC			Voltage DC current

# References

| [1] | ESS-0149550, “Operations personnel roles and responsibilities in the ESS Main Control,” [Online]. |
| --- | --- |
| [2] | ESS-0134492, “ESS-0134492-Concept of Operations For the Accelerator Personnel Safety System 0 (PSS0),” [Online]. |
| [3] | ESS-0237967, “ESS-0237967 PSS0 Hardware Design Requirements Specifications,” [Online]. |
| [4] | S. p. Supplies, 11.2016 A5E37775406-7-76. |
| [5] | ESS-0242842, “ESS-0242842 ESS RULES FOR ELECTRICAL LOCK-OUT/TAG-OUT,” [Online]. |
| [6] | ESS-0151602, “ESS-0151602 Accelerator PSS0 Electrical Circuit Diagram,” [Online]. |
| [7] | ESS-0058389, “Personnel Safety System Configuration Management Plan,” [Online]. |
| [8] | ESS-0322494, “Proof Test for PSS0,” [Online]. |
| [9] | ESS-0325736, “System, Key List for PSS0 Key Exchange,” [Online]. |
| [10] | ESS-029088, “ESS-029088 Hazard and risk analysis,” [Online]. |

# Document Revision history

| Revision | Reason for and description of change | Author | Date |
| --- | --- | --- | --- |
| 1 | First issue | Mattias Eriksson | 2018-06-28 |