## Risk List
| EXCELONAUT® |  |  |  |  | H01 | [14 empty] | Probability
Risk List - Lichtenberg method
[5 empty] | Rev. date: | 2019-01-22 MHE | [18 empty] | 0= 1 gång på 1000 år, 0,05
All costs in SEK, VAT excluded.
| 1. Risks | Risk owner | Unit | Min | Probable | Max | Probability (0,5-90%) | Personal Injuries (1-5) | Annual operation cost (1-5) | Goodwill (1-5) | Quality and function (1-5) | Stillestånd Downtime (1-5) | Property damage (1-5) | Surround- ings(1-5) | Expected cost | Standard dev. | Variance | Priority (%) | Mitigation | Comments | Personal injuries | Downtime
[22 empty] | 1 | <1h
[22 empty] | 2 | dag
1.1 | Kraftringen part of scope 1: Pipe rupture: stop on all pumps->non operational accelerator->Problems with Kryo | ESS | SEK |  |  |  | 0.05% |  |  |  |  | 3 |  |  | 0 | 0 | 0 | #DIV/0! | Create ways of communication between ESS and Kraftringen in the operations phase. Seperate expansion tank and to top up with tapwater is a possible mitigation. Should the ESS review comittee decide on the matter? |  |  | 3 | vecka
1.2 | Kraftringen part of scope 2: Pressure regulating pumps are shut down by mistake in the district heating network -> E.ON can operate the pumps, 1h downtime. Accelerator not operational. | ESS | SEK |  |  |  | 0.5% |  |  |  |  | 1 |  |  | 0 | 0 | 0 | #DIV/0! | Create ways of communication between ESS and Kraftringen in the operations phase. Seperate expansion tank and to top up with tapwater is a possible mitigation. Should the ESS review comittee decide on the matter? |  |  | 4 | månad
1.3 | Kraftringen part of scope 3: Temperature rises above 60C, At 70C we loose 60-70%. Consequence: we loose parts of the cooling effect | ESS | SEK |  |  |  | 0.5% | [7 empty] | 0 | 0 | 0 | #DIV/0! | RER: Prioritisation of cooling may be needed. To be further investigated. |  |  | 5 | >mån
1.5 | Kraftringen part of scope 5: Pressure differences that deviate from design pressure, what´s the effect? Systems are designed to avoid a hard stop. Measure: Pumps slow down, use cooling tower. In principal no consequences. | ESS | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | To be monitored
1.6 | Kraftringen part of scope 6: Contaminations in the supply line from Kraftringen. Measure: Install filters. Consequence: valves and pumps may malfunction. | E.ON | SEK |  |  |  | 65% |  |  |  |  | 2 |  |  | 0 | 0 | 0 | #DIV/0! | MEM: Add a filter to the system in design. |  | Annual operation cost | Surroundings
1.7 | Kraftringen part of scope 7: Possible issue regarding singal exchange with Kraftringen. Currently there´s no such system, but we should be able to see each others production/consumption. | E.ON | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | To be monitored
1.8 | Miscellaneous: Could the outside temperatures fall to low? HVAC is designed for -18C, sprinkler for - 40C 1/10000. | E.ON | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! |  | Design enligt "normala" förutsättningar gäller.
1.9 | Inside the CUB: 1. Pipe rupture will lead to hot water release and flooding. Consequence: destroyed equipment, risk of casualty | E.ON | SEK |  |  |  | 0.5% | 5 |  |  |  | 2 |  |  | 0 | 0 | 0 | #DIV/0! | MEM: Measures: check the system before operation start. Install collision protection in suitable locations.
1.10 | CWH: 1. User side: no incoming flow, what´s the consequence. No consequence. | E.ON | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.11 | CWH: 2. Malfunctioning heat exchanger->Leakage, needs to be replaced, close the circuit. By-pass missing. Currently a planned stop is needed to replace it, roughly one day of work. | E.ON | SEK |  |  |  | 65% |  |  |  |  | 2 |  |  | 0 | 0 | 0 | #DIV/0! | MEM: Add a by-pass, or alternatively two heat exchangers that can be changed without stop in operations.
1.12 | CWH: 3. Two heat exchangers malfunction. Means that kryo will stop working. | E.ON | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.13 | CWH: 4. District heating water leaks into the system through a broken heat exchanger. Prob 1/1000. Contamination of the district heating water or refrigerant? Measure the conductivity? AD measures the conductivity in the system. How much conductive water is allowed to enter the system before the system in total is effected? INVESTIGATE! Roughly a week is needed to flush the whole system, identifying the leak is a larger issue. Measure: filters are already installed in the system | E.ON | SEK |  |  |  | 0.5% | [7 empty] | 0 | 0 | 0 | #DIV/0! | Kenneth & Anton: Investigare the issue with conductivity and if more filters are needed. Install a more reliable exchanger. Add a conductivity measurer
1.14 | CWH 45 C: 5. Pump malfunctions? n+1 pumps are installed, it takes an estimated 20 seconds to start the redundant pump, which happens automatically. Should not effect the whole system. | E.ON | SEK |  |  |  | 35% | [7 empty] | 0 | 0 | 0 | #DIV/0! | . | Bra skyddsnivå | Goodwill |  | Property damage (kostnad att återställa anläggning)
1.15 | Loss of power for longer duration to TRAFO. Solution; pumps should be connected to different TRAFOs. | ESS | SEK |  |  |  | 35% |  |  |  |  | 1 |  |  | 0 | 0 | 0 | #DIV/0! | RER: Investigate if vulnerable parts of ESS need emergency power. |  |  |  | 1 | <100 000
1.16 | Ackumulator tank is damaged? Possible to bypass, the adjustement accuracy is lost. No consequence for the rest of the system. | E.ON | SEK |  |  |  | 0.05% | [7 empty] | 0 | 0 | 0 | #DIV/0! | - |  |  |  | 2 | 1000000
1.17 | A heating pump falters. User side get´s disconnected. Connection downwards can handle a falting pump. No consequece. | E.ON | SEK |  |  |  | 35% | [7 empty] | 0 | 0 | 0 | #DIV/0! |  |  |  |  | 3 | 10 MSEK
1.18 | One out of several valves seizes in closed posistion. Loss of effect, if it´s during maximum load there´s no issue. Emergency cooling on roof will help. | ESS | SEK |  |  |  | 35% | [7 empty] | 0 | 0 | 0 | #DIV/0! | RER: Prioritisation of cooling may be needed. To be further investigated. |  |  |  | 4 | 100 MSEK
1.19 | CWM 25 C. AD:s sensitivity is +-1 C,what happens > +- 2 C- modulator shuts down. At >+- 4-5 C the circulator malfunctions -> will trip the accelerator. Three pumps might be needed? TO BE INVESTIGATED! |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | MEM and Anton to investigate. |  |  |  | 5 | >100 MSEK
1.20 | Radioactive leakage. Our system has a higher pressure. Target Division has an intermediate system. Far-fetched that it will have an effect on our system. We are missing a signalsystem to be able to identify any leaks. Exchange of signals with Target Division should be set up | E.ON | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | Create a signal exchange between E.ON, Target Div and Acc Div.
1.21 | CWL. Valve falters in closed position. Measure: investigate if two valves should be installed to the circulating heating pump.? | E.ON | SEK |  |  |  | 35% |  |  |  |  | 1 |  |  | 0 | 0 | 0 | #DIV/0! | MEM: Investigate the possiblity of installing dual valves. |  | Quality and function
1.22 | Miscellaneous: Sectioning of the CUB? What happens in case of fire? All the heating pumps are placed in the same room. Investigate: fire scenario and also gas evacuation of refrigerant. | E.ON | SEK |  |  |  | 0.5% | [7 empty] | 0 | 0 | 0 | #DIV/0! | MEM Fire analysis to be made.
1.23 | Other systems that have not been investigated: compressed air, deionization |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.24 | Compressed air: different scenarios have been investigated: powersupply, redundancy exists via the different trafos. Is backup power needed for compressors in order to operate valves? No, there´s no need to manipulate valves. What happens in case of pipe rupture? Handable, only 50 % capacity if this occurs. Compressor tank can not be by-passed. Redundancy is achieved through the rest of the system. |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | A superior control system for E.ON and ESS compressed air that ensures that these two systems don´t work againt each other. There´s also a possiblity to connect a rented system on the compressor tank if needed.
1.25 | Cooling of the compressed air system: The system is based on that cooling and compressed air shall be avaliable at the same time, which it won´t be. What do we do with the excess heat? Geothermal cooling can be used. ALU to investigate. |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.27 | Deionized water: The system can produce 2 m3/h. E.ON needsto know if the consumption is correct? Waste building also needs deionized water. Could this equipment be placed in H09? ALU investigates |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0! | MEM: Increse the dimension of the domestic water piping in slab from 1" to 2".
1.28 | Deionized water: The facility will not receive domestic water. No consequence, the facility can manage without deionized water for a while. The system will also be shut down during maintenance. The facility is not system critical, no downtime will be created. |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.29 | Deionized water: N2-emissions in the facility. No hazard. |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.31 |  |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.32 |  |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.33 |  |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.34 |  |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!
1.35 |  |  | SEK | [11 empty] | 0 | 0 | 0 | #DIV/0!