## Slide 1: Fire Safety in Laser Labs at Jefferson Lab
International Technical Safety Forum
2019
European Spallation Source
Lund, Sweden
Bert Manzlak, CSP

## Slide 2: U.S. National Laboratories

## Slide 3: Thomas Jefferson National Accelerator Facility
Jefferson Lab Newport News, Virginia
Its primary mission is to enable basic research for building a comprehensive understanding of the atom’s nucleus
12 GeV Electron Beam Accelerator
~1,400 meters CEBAF Four Experimental Halls
~ 750 Staff
~ 1,500 Users (~ 200 daily)
~ 200 Students (~100 daily)
Class 4 or 3B Laser Labs - 18

## Slide 4: Jefferson Lab

## Slide 5: Government Requirement
Department of Energy
10 C.F.R. 851
Workers Safety and Health Plan
General requirements —
Contractors must provide a hazard free place of employment and ensure that all work performed is in compliance with the worker safety and health program.

## Slide 6: Consensus Laser Standard & Fire Code
2016 Edition

## Slide 7: ANSI Z136.1 - 2014 Safe Use of Lasers
Section 7.2.3 Fire Hazards
Class 4 laser beams represent a fire hazard.
Enclosure of Class 4 laser beam can result in potential fire hazards if enclosure materials are likely to be exposed to irradiances exceeding 10·W cm-2 or beam powers exceeding 0.5 W.
Under some situations where flammable compounds or substances exist, it is possible that fires can be ignited by Class 3B lasers.
NOTE – The National Fire Protection Agency standard NFPA ® 115 states that for continuous wave (CW) lasers, 0.5 W·cm-2 is a possible ignition hazard.

## Slide 8: Jefferson Lab Policies
ES&H Manual Chapter 6410 Laser Safety Program
Mitigate hazards posed by lasers
ES&H Manual Chapter 6900 Fire Safety Program
Minimize losses from fire

## Slide 9: Fire Safety Objective
Life Safety
Access during an emergency
  Medical
  Fire
  Other crisises
Egress from laser lab to exits
  Primary & Secondary exits
  Lab equipment / walkways
  Laser barriers, curtains

## Slide 10: Fire Prevention Control Systems
Smoke Detection
Heat Detection
Alarms

## Slide 11: Fire Suppression Systems
Fire Suppression Equipment
  Automated - General or Local
  Manual

## Slide 12: Laser Fire Safety Objective
Avoiding hazardous conditions from fire in:
Laser components, Optical paths, Target and Lab materials
Clothing of persons in or near laser laboratories
Building materials
Ignition of flammable chemicals and gases
Production of smoke, irritants or toxins

## Slide 13: General Laser Fire Hazards
  Class 4 lasers
  Lab building materials
  Combustible and flammable materials
  Class 3B lasers under certain conditions

## Slide 14: Laser Fire and Ignition Hazards
Combustible Material
  Class 4 lasers
  Typical office, lab, building materials
Flammable Material
  Class 3B lasers
  Create flammable atmosphere
  Small ignition source needed

## Slide 15: General Laser Fire Hazards
Combustible materials in labs
  Room, building construction
  Laser table, barriers, curtains
Ignition issues in labs
  Flammable chemicals / material
  Ignition sources

## Slide 16: Specific Fire and Ignition Hazards
Ignitable chemicals
Flammable gases & vapors
Unusual targets

## Slide 17: Laser Classifications of Concern
A Class 4 laser beam can cause materials to smolder or burn, especially at close range
Under some situations where flammable compounds or substances exist, it is possible that fires can be ignited by Class 3B lasers

## Slide 18: Standard Engineering Controls
Beam Stop or attenuation
Beam Shutters
Controlled Beam Path
Protective Housing

## Slide 19: Jefferson Lab Administrative Control
Laser Operational Safety Procedure (LOSP) for all
Class 4 & Class 3B
lasers or laser systems

## Slide 20: Laser Fire Safety - Key Personnel
Fire Marshal
Laser Safety Officer
Laser System Supervisor
Laser Operator
Area Safety Warden

## Slide 21: Fire Marshal
Perform authority having jurisdiction (AHJ) authorities
Ensure the fire protection program is reviewed, assessed and implemented
Serve as Subject Matter Expert (SME) for the fire-protection systems

## Slide 22: Laser Safety Officer
Perform laser equipment / area hazard evaluations
Approve LOSPs
Perform an ESH&Q Review on all lasers and equipment purchase requests
Approve acceptable procurement requests
Monitor and enforce hazard control requirements for laser systems

## Slide 23: Laser System Supervisor
If supervising inexperienced workers, develop an equipment / area specific laser mentor program
Maintain a list of Qualified Laser Workers for specific equipment / areas
Perform Laser Safety Control Inspections (Bi-Annual Formal)

## Slide 24: Laser System Supervisor

## Slide 25: Laser Operator
Maintain current training (SAF 114O Laser Orientation), and specific training as determined by the Laser System Supervisor
Request an equipment / area hazard evaluation from the Laser Safety Officer if compliance with requirements is unclear

## Slide 26: Safety Warden
Perform documented Safety Warden Inspections - Monthly
  Inspect portable fire extinguishers
  Inspect means of egress
  Inspect area housekeeping
  Inspect flammable storage

## Slide 27: What More
Annual Building Fire Exercise
Test Alarms
Evacuation
Muster Points (designated area for accountability after evacuation)
Municipal Fire Department Information Exchange
Emergency Management Exercises
Building Hazard Highlight Discussions - Lasers

## Slide 28
manzlak@jlab.org
Bert Manzlak, CSP
The Fire Safety Program in Laser Labs … Works!

## Slide 29
Back-Up Slides

## Slide 30: Jefferson Lab Street Hockey
Hall A

## Slide 31: A Bit of Laser Classification Information
Class 3B
Lasers in this class may cause damage if the beam enters the eye directly. This generally applies to lasers powered from 5–500 mW.
Lasers at the high power end of this class may also present a fire hazard and can lightly burn skin.
Class 4
By definition, a Class 4 laser can burn the skin, or cause devastating and permanent eye damage as a result of direct, diffuse or indirect beam viewing.
These lasers may ignite combustible materials, and thus may represent a fire risk.

## Slide 32: ANSI Z136.1 – 2014 “Safe Use of Lasers”
Section 7.2.3 Fire Hazards
Class 4 laser beams represent a fire hazard.
Enclosure of Class 4 laser beam can result in potential fire hazards if enclosure materials are likely to be exposed to irradiances exceeding 10 W cm2 or beam powers exceeding 0.5 W.
Under some situations where flammable compounds or substances exist, it is possible that fires can be ignited by Class 3B lasers.
NOTE – The National Fire Protection Agency standard NFPA ® 115 states that for continuous wave (CW) lasers, 0.5 W cm-2 is a possible ignition hazard.

## Slide 33: A bit more about Class 3B lasers
Class 3B
A Class 3B laser is hazardous if the eye is exposed directly, but diffuse reflections such as those from paper or other matte surfaces are not harmful.
The AEL for continuous lasers in the wavelength range from 315 nm to far infrared is 0.5 W.
For pulsed lasers between 400 and 700 nm, the limit is 30 mJ.
Other limits apply to other wavelengths and to ultra-shot pulsed lasers.
Protective eyewear is typically required where direct viewing of a class 3B laser beam may occur.
Class-3B lasers must be equipped with a key switch and a safety interlock.
Class 3B lasers are used inside CD and DVD writers, although the writer unit itself is class 1 because the laser light cannot leave the unit.
Class 3B visible-beam lasers are medium powered, from 5 to 499 milliwatts.
A Class 3B laser can cause eye injury. The more powerful the laser, the greater the chance of injury.

## Slide 34: A bit more about Class 4 lasers
Class 4
Class 4 is the highest and most dangerous class of laser, including all lasers that exceed the Class 3B Allowable Exposure Limit (AEL).
These lasers may ignite combustible materials, and thus may represent a fire risk.
These hazards may also apply to indirect or non-specular reflections of the beam, even from apparently matte surfaces – meaning that great care must be taken to control the beam path.
Class 4 lasers must be equipped with a key switch and a safety interlock.