## Slide 2: Environmental concerns from design to operation of a new electrical substation
ITSF 2019 - Lund
Presented by S. Schadegg - CERN

## Slide 3: The new substation
LHC
SPS
New substation
Existing substation

## Slide 4: The new substation
Existing CERN substation
New CERN substation
400 kV Entry point
220 MVA Transformer
66 kV starting point
The operating building

## Slide 5: The new substation
The transformer characteristics:
  220 MVA
  224 tons
  10*4*16 meters
  82’000 liters of oil

## Slide 6: Environmental aspect of a substation
Design
Noise
Electrical & Magnetic Fields
Water resources (qualitative & quantitative)

## Slide 7: Environmental aspect of a substation
Design
Noise
Electrical & Magnetic Fields
Water resources (qualitative & quantitative)

## Slide 8: Environmental aspect of a substation
Design
Code de la Santé Publique R.1334-30:
Daytime (7 a.m. to 10 p.m) : emergence limits 5 dB (A)
Night time (10 p.m. to 7 a.m.) : emergence limits 3 dB (A)
Noise Level of the transformer (including fans) : 88 dB (A)
4 walls arround the transformer
 < 1dB (A) of the noise emergence
Noise
Electrical & Magnetic Fields
Water resources (qualitative & quantitative)

## Slide 9: Environmental aspect of a substation
Design
No emission of Electrical fields (underground power lines)
Negligible Magnetic fields (19 µT, 1m above the soil)
Noise
Electrical & Magnetic Fields
Water resources (qualitative & quantitative)

## Slide 10: Environmental aspect of a substation
Noise
Electrical & Magnetic Fields
Water resources (qualitative & quantitative)
Design
Hydraulic study:
49 m3 retention + <10 l/s flow release
(HC detector)

## Slide 11: Environmental aspect of a substation
Design
Deported pit
Retention basin
Transfo.
filters
Oil separator
CERN network
pits
Scenario 1: Normal running

## Slide 12: Environmental aspect of a substation
Design
Deported pit
Retention basin
Transfo.
filters
Oil separator
CERN network
pits
Scenario 2: leak of the 100% of the transformer oil
50 m3
80 m3

## Slide 13: Environmental aspect of a substation
Design
Deported pit
Retention basin
Transfo.
filters
Oil separator
CERN network
pits
Scenario 3: leak of the 100% of the transformer oil with a fire
50 m3
80 m3
200 m3
82 m3 oil
120 m3 extinguishing water
49 m3 Rain water
Notes: 80 m3 in addtion

## Slide 14: Environmental aspect of a substation
Worksite
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances

## Slide 15: Environmental aspect of a substation
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances
Worksite – on the paper

## Slide 16: Environmental aspect of a substation
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances
Worksite – on the paper

## Slide 17: Environmental aspect of a substation
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances
Worksite – on the field

## Slide 18: Environmental aspect of a substation
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances
Worksite – on the field
CERN Water monitoring station

## Slide 19: Environmental aspect of a substation
Air
Waste management
Natural resources
Water resources (qualitative)
Soil protection
Other nuisances
Worksite – on the field

## Slide 20: Summary

## Slide 21
“ Olive is designed to respect the strictest environmental standards, and its specially constructed noise-cancellation panels make it extremely quiet for a power transformer of its size. In addition, the new BE2 electrical substation contains an advanced oil-retention and ﬁre-suppression system to protect the environment in the unlikely event of a ﬁre or an oil leak.”
Conclusion (1/2)

## Slide 22: Conclusion (2/2)
Many challenges (land acquisition, no detailed technical prescriptions for the environmental protection, tricky cohabitation with Travellers,...) overcame by a good internal collaboration with the project team and the Safety specialists.
Accident scenarii shall be assess from the beginning to detail the requirements included in the Technical Specification.
 Principles of the retention scenarii involving oil and fire extinguishing water will be applied to other similar projects

## Slide 23
Thanks for your attention!
Sabrina Schadegg
Sabrina.Schadegg@cern.ch CERN HSE Unit
Environmental Engineer Tel +41 22 766 30 39 Port +41 75 411 70 33