## Slide 2: SPS FIRE Project A major fire safety consolidation in an aging facility
ITSF 2019 (ESS)
Art Arnalich (CERN HSE-OHS-IB) on behalf of CERN Fire Safety Engineering Team
Contributions from Florence Pirotte (CERN BE)
Notes: The SPS FIRE Project: a major fire safety consolidation in an aging facility to face future challenges. "
The Super Proton Synchrotron (SPS) is the second largest accelerator at CERN, a 450 GeV proton and heavy ion machine serving the North Area experimental area and playing a key role as an injector for the LHC (Large Hadron Collider). Commissioned in 1976, the SPS featured a fire safety concept dating from the 70’s, that remained unchanged until today and for which CERN management launched a fire safety consolidation study in 2015.
This presentation explores the findings of the consolidation study, the challenges of a fire safety consolidation project of a 40-year-old research machine and some of the lessons learned by CERN Fire Safety Engineering Team.
From a very early stage, the fire risk assessment carried out during the study phase, revealed a number of shortcomings in life safety objectives: occupant protection and firefighter safety did not comply with current standards and best practices. In addition, low levels of property protection showed not only potential damage beyond the SPS into upstream machines like the PS (Proton Synchrotron) but also a risk to the continuity of operations of machines and experimental areas located downstream the SPS.
In the absence of applicable or fit-for-purpose fire safety codes for large underground research facilities, technical solutions went through a Performance-Based Design exercise benchmarking potential trial designs with the existing situation. As in any retrofit project, operational and maintenance constraints factored heavily in the adopted solution which outstands as best effort from all stakeholders to reach a balanced result between operations, fire safety and budget.
A final word focuses on the lessons learned by CERN Fire Safety Engineering Team in this 11 million € fire safety project which stands as the largest and most ambitious fire safety initiative carried out at CERN.

## Slide 3: The SPS FIRE Project
Scope
Need
SPS FIRE Study
SPS FIRE Project
Solution
Procurement
Implementation
Operation
Jan
2015
Sept 2016
Dec 2018
Aug
2020

## Slide 4
CERN Super Proton Synchrotron
Scope
second largest CERN machine
450GeV, protons / ions
7km, 60m deep, 4.5m diameter
commissioned 1976
1970 fire safety standards

## Slide 5
CERN Super Proton Synchrotron
Scope

## Slide 6
1976
2016

## Slide 7
early days
2014

## Slide 8: Fire Safety Concept evolution SPS example
acceptable risk level (*)
1976
2016
SPS risk level
SPS FIRE Project
~13MCHF
(*) acceptable risk levels evolve with risk acceptance by society, state of technology, incident experience, resilience expectations, evolution of costs of discontinuity of operations among other factors.
Need

## Slide 9: Current SPS layout
1.1 km
Need

## Slide 10
1.1 km
Current SPS layout
Need

## Slide 11: Accessible areas for firefighting Current situation
Need

## Slide 12: Study phase
Jan 15 SPS Fire Safety Study is launched
triggered by a need of the fire service (HSE-FB)
endorsed/supported by facility risk owner (EN DSO)
led by facility operators (BE-OP)
multiple participants: radio protection, fire expertise,
emergency preparedness, environment, transport,
implementation actors, service providers….
Need
SPS FIRE Study

## Slide 13: Fuel load, extinguishing means
SPS FIRE Study

## Slide 14
t=0min
t=7min
t=30min
Evacuation conditions
SPS FIRE Study

## Slide 15
Uncontrolled radioactive release
SPS FIRE Study
Fuel load burnt resulting in a dose in members of the public above 0.3 mSv
100 kg

## Slide 16
  Evacuation conditions to be improved
  Firefighter safety to be improved
  Search and rescue operations likely to fail
  Limited control of activated smoke
  Large property damage is plausible
  Critical impact in continuity of operations
Findings
SPS FIRE Study

## Slide 17
SPS FIRE Study
SPS FIRE Project
13.1 MCHF
Clear mandate to solve findings of SPS Study
Time framing for LS2

## Slide 18: SPS FIRE Project strategy
Compartmentalization by means of fire doors
Fire suppression system (sprinkler) in high fuel load areas
Integrated safety control system for fire detection, alarm, evacuation, ventilation control and fire door control
Fire attack means to ensure firefighter safety and intervention: dry riser and firefighting tractors/trolleys
SPS FIRE Project
Notes:     to protect evacuation routes
    to supress fire early by sprinkler activation
    to allow firefighter deployment for search&rescue and fire attack
    to isolate SPS from other facilities
    to protect/isolate high activation areas

## Slide 19: SPS FIRE Project strategy
The proposed solution is a balance between fire safety, infrastructure and operation in a retrofit scenario.
All fire safety elements are foreseen as complementary systems.
Partial or stand-alone implementations involve degraded fire protection scenarios.
SPS FIRE Project
Notes:     to protect evacuation routes
    to supress fire early by sprinkler activation
    to allow firefighter deployment for search&rescue and fire attack
    to isolate SPS from other facilities
    to protect/isolate high activation areas

## Slide 20
52 fire doors in different priority levels (colors)
Compartmentalization
SPS FIRE Project

## Slide 21
Compartmentalization
SPS FIRE Project

## Slide 22: Accessible areas for firefighting
SPS FIRE Project

## Slide 23
Firefighting means in every shaft
SPS FIRE Project

## Slide 24
Dry riser covers entire facility
Dry by default, only filled with water in case of intervention
Dry riser for firefighter intervention
SPS FIRE Project

## Slide 25
Dry riser for firefighter intervention
SPS FIRE Project

## Slide 26: Fire detection and safety actions
Air aspiration smoke detection covers entire facility
6 safety zones covering the entire facility for evacuation and compartmentalization
SPS FIRE Project

## Slide 27: Fire detection and safety actions
SPS FIRE Project

## Slide 28: Sprinkler system
Covers shafts, TAs and LSSs
SPS FIRE Project

## Slide 29
Without sprinklers
630GJ
0.9
~20000kg plastic burnt
E=630GJ, Hc=30MJ/kg, probability 90%
TA/LSS with/without sprinkler
SPS FIRE Project

## Slide 30
Without sprinklers
630GJ
0.9
1GJ
0.9
With sprinklers
~20000kg plastic burnt
E=630GJ, Hc=30MJ/kg, probability 90%
~35kg plastic burnt
E=1GJ, Hc=30MJ/kg, probability 90%
TA/LSS with/without sprinkler
SPS FIRE Project

## Slide 31
Sprinkler system
SPS FIRE Project

## Slide 32
The Launch Safety Agreement (LSA) covering the conventional safety aspects for all WPs.
One Safety File for each WP (4) with :
  the descriptive part (= purpose and motivation, location, safety system, life cycle of the project)
  the demonstrative part (= risk assessment and mitigation measures)
  the operational and REM (=REX) parts: after commissioning, when system in operation -> Safety procedures to operate, mand Safety related records: reports, lessons learned, changes, non- conformity, maintain, dismantle, dispose (incident/accident reports)
Prevention Plan for the installation phase: document defining all the measures for the prevention of risks.
Documentation organization
(F. Pirotte BE)

## Slide 33
Largest and most ambitious fire safety consolidation carried out at CERN.
Full endorsement and support of CERN management.
Considerable effort from SPS-FIRE to adapt to constraints to be obtained after full implementation.
HSE support during design and works remains essential.
Conclusions

## Slide 34
Success in fire safety
is driven by team work and excellence
in fire education, fire research, fire prevention, fire protection,
fire codes, fire safety engineering, firefighter training, ... and fire operations.
Thanks for your attention!