## Slide 2: International Technical Safety Forum ITSF 2019 13th May 2019, European Spallation Source The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN Giordana Gai, HSE-OHS-IB FSE team on behalf of the FIRIA team
EDMS 2149906 v.1
Giordana Gai

## Slide 3: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Outline
Introduction
Project organization
First FIRIA pilot case
Conclusions
Giordana Gai

## Slide 4: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Fire Risk Assessment
Exercise to assess the safety outcome in case of fire of a facility with a given fire protection concept.
Life
  occupants
  victims
  first responders
Environment
Property
Continuity of operation
Giordana Gai
Art Arnalich

## Slide 5
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
Code compliance
Prescriptive
Multiple methodology choice:
Art Arnalich

## Slide 6
EDMS 2149906 v.1
LHCb
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
Risk based
Qualitative
Quantitative
Multiple methodology choice:
Art Arnalich

## Slide 7
EDMS 2149906 v.1
Current limitations
      Radiological risk induced by a fire event not encompassed or overestimated
      (100% transport assumption)
Public
Fire Service
Environment
?
?
?
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
Art Arnalich

## Slide 8
EDMS 2149906 v.1
Giordana Gai
Art Arnalich

## Slide 9
EDMS 2149906 v.1
?
?
?
Giordana Gai
Art Arnalich

## Slide 10
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
Current limitations
      Radiological risk induced by a fire event not encompassed or overestimated
      (100% transport assumption)
      In addition:
      Using a probabilistic approach (risk methodology) instead of a scenario analysis
      Including cost benefit analysis in the procedure of risk assessment e.g. when proposing mitigation measures

## Slide 11
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
10 team members
Cross CERN HSE sinergies (OHS, RP, FB)
Collaboration with CERN CFD team and IT colleagues
Timeline
Jan 2018  Jun 2021
HSE-OHS-IB
HSE-OHS-IB
HSE-OHS-IB
HSE-OHS-IB
HSE-OHS-IB
HSE-RP-AS
HSE-OHS-IB

## Slide 12
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
WP-I Implementation and Communication
Art Arnalich
Exhange with safety actors and stakeholders at CERN
Feedback was collected and taken into account for the definition of the Users Requirements
List of pilot cases has been proposed and accepted by the project board

## Slide 13
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
WP-A Aerosol
Oriol Rios
A number of combustible items were tested at the Fire and Aerosol laboratories of Lund University
More appropriate design fires (HRR, soot yield)
Number and mass distribution of the soot
Aerosol deposition modelling in FDS (NIST & Jensen Hughes)
WP-T Testing
Fabio Corsanego

## Slide 14
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
WP-R Radiation Protection
Pavol Vojtyla
Sameh Melhelm
Uwe Kauflin
Fabio Pozzi
Three main activities:
Activity level inside the facility (FLUKA calculations)
Outdoor dispersion and deposition modelling
Dose calculation to the public and environmental assessment

## Slide 15
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
WP-M Methodology
Giordana Gai
Development of a probabilistic framework of risk assessment wrt life safety, property protection and enviroment
Frequency analysis
Consequence analysis
Cost benefit analysis
Supervision of
H. Frantzich and E. Ronchi

## Slide 16: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
ISOLDE: Isotope Separator On Line DEtector
Ongoing analysis of the first FIRIA pilot case

## Slide 17: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
ISOLDE
target area
838
355m2
1065m3
BTY line
834
40m
ISOLDE: Isotope Separator On Line DEtector

## Slide 18: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Vacuum pump
Beamline (magnets, cable trays)
Hazard identification

## Slide 19: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Two robots
Tanks
Target storage
Tanks
Hazard identification

## Slide 20: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Oil + cable tray fire
Cable tray fire
Robot fire
Three main scenarios have been identified and will be analysed under different conditions i.e. considering the failure on demand of fire safety systems
Total: 12 runs of FDS
Selection of representative design fire scenarios

## Slide 21: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Oil + cable tray fire (run 03)
Cable tray fire (run 07)
Robot fire (run 11)
Screenshot at t = 4 min
Smoke propagation in the facility under failure of the closing device of the doors

## Slide 22: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Screenshot at t = 4 min
Soot deposition in the facility under failure of the closing device of the doors
Indoor modelling
Life safety of occupants
Property protection
Fire Brigade intervention

## Slide 23: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Indoor modelling
Life safety of occupants
Property protection
Fire Brigade intervention
Smoke release to the environment
(less than the initial assumption of 100 % transport!)

## Slide 24: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Outdoor modelling
Environmental dispersion
Dose calculation

## Slide 25: Conclusions
EDMS 2149906 v.1
Giordana Gai
International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
A number of international collaborations have been set up:
FCC fire safety study collaboration  FIRIA collaboration
Lund University
Methodology development
Testing campaign of combustible items
Italian Fire Services
Meyrin geometrical model in FDS
NIST
New features implemented in FDS driven by FIRIA needs
Investing in an experimental campaign to further validate the deposition model

## Slide 26: International Technical Safety Forum 2019, Session “Fire Safety” The FIRIA project: an integrated approach to address fire and fire-induced radiological release risks at CERN
EDMS 2149906 v.1
Giordana Gai
Conclusions
Jul 2019: assessment of the ISOLDE target area (pilot case 1) will be presented to the project board
Dec 2019: assessment of pilot cases 2 and 3
----- LESSON LEARNT -----
Jun 2020: Refinement of the methodology based on CERN needs
From Jun 2020 on: FIRIA Production line is established