## Slide 1: Question today imagine tomorrow create for the future
Daniel Rosberg, Technical Director, Fire & Risk

## Slide 2: The Bunker
Provides a shielding structure around the monolith
Part of Experimental Hall D01 and D03
Radius 15/28 m.
5 m high
310+330 m2 roof footprint area
VKR 100x100x8
VKR 100x100x10
Utilization factor 0.5
3- and 4-side exposure
Structural Steel

## Slide 3: The Requirements
Provided by the Swedish building regulations, EKS
Bunker is part of the experimental halls and BSK is adopted from a high building classification
Fire load density
Fire safety classification (Bsk)
Design fire exposure (temperature)
Requirements
Design
Temperature domain
Mechanical behavior
Fire protection

## Slide 4: Fire load density
12 instruments (8 long and 4 short) are assumed.
A total amount of 1600 kg plastics is introduced by the instruments.
Shielding material is (Mirrobor) consist of 20% combustibles (plastic).
Three different values on the amount of shielding material are presented for each bunker:
  A low estimate (only optics shielded)
  A realistic estimate (Optics+side+½ rear of the instruments)
  A worst case (Optics+side+rear+roof+floor of the instruments)

## Slide 5: Sprinkler
Sprinkler inside the bunker
Rescue service operation inside bunker is difficult
Defense in depth
Safe egress
Reduce fire load
…
Provides some reduction if fire protection is designed using the classification method
Low and realistic estimate on shielding = R60 (no effects of sprinkler)
High estimate on shielding = R90 (R120 without sprinkler)
Fire load density may be reduced to 60% using the design method of a natural fire

## Slide 6: Analysis of a natural fire
Method by European standard SS-EN 1991-1-2 to find the temperature exposure
Takes several parameters into consideration
  Building geometry
  Fire load density
  Surrounding materials
  Opening factors
  Sprinkler
Steel temperature can be calculated using European standard SS-EN 1993-1-2
  Critical temperature 585°C

## Slide 7: The results
Low and realistic estimate
No sprinkler
  Critical temperature is exceeded
With Sprinkler
  Low steel temperature in the fully developed fire (<585°C)
  Localized fire
  The localized fire will require a safety distance or fire insulation
Worst case estimate
No sprinkler
  Fuel load density >800 MJ/sqm
  High (steel) temperature
  R120 using classification method
With sprinkler
  Fuel load density >800 MJ/sqm
  High (steel) temperature
  R120 using classification method

## Slide 8: The future
Determine the exact amount of shielding
Possibility to use safety distances to fire sources
Decide on the means of protection
Or
Back to basics and the possibility to revise the fire safety classification of the steel members

## Slide 9: Thank you!
wsp.com