## Slide 1: Lessons Learned from Testing and Commissioning of the Ion Source and LEBT
Saeed Haghtalab
www.europeanspallationsource.se
2019-08-28
Control System Integration
Notes: sada

## Slide 2: Outline
ISrc-LEBT Control System
  Catania
  Lund
Lessons learned from:
  In-kind collaboration
  Organization
  Planning
  Preparation and execution
  Administration
  Interfaces
Summary

## Slide 3: ISrc-LEBT Control System Catania
MC Motion Controller
PLC Programmable Logic Controller
VME Versa Module Eurocard bus
MTCA Micro Telecommunication Computing Architecture
IPC Industrial Personal Computer

## Slide 4: ISrc-LEBT Control System Lund
MC Motion Controller
PLC Programmable Logic Controller
VME Versa Module Eurocard bus
MTCA Micro Telecommunication Computing Architecture
IPC Industrial Personal Computer

## Slide 5: In-kind Distributed team
5
INFN-LNS
In-kind contributor for the ISRC and LEBT
ESS
Accelerator Division
ICS Division
CEA
In-kind contributor for the control system
ESS
CEA
INFN-LNS

## Slide 6: In-kind
ISrc, LEBT and associated control systems delivered as a consistent (with FAT) and tested unit.
Good collaboration with in-kind partner in a constructive and friendly manner.
Ensure well-defined requirements and standards and close interaction with in-kind partner prior and after delivery to ensure fully documented configuration and comprehensive well-documented FAT and SAT.
Reinforce
Improve
Structure, processes and standards were not fully defined since the beginning.
FAT and SAT were not fully conducted and documented.
Documentations (system design, configuration etc.) were not fully completed and reviewed.
Notes: - Isrc controls delivered as a consistent and tested unit as we sometimes say … but it was working in Catania ...
- There was a very good collaboration between us and in-kind. They were open to help us and answer our questions regarding iris and emu even though it was a long time since they were working on it and they couldn’t remember the details exactly.
- Many of the current ICS standards that we have now were not exist at the time of the isrc controls in-kind contract. This is obvious from the changes we saw in previous slides.
We didn’t perform FAT and SAT completely. Due to unavailability of infrastructure in first few months and the configuration change afterwards.
Many documents were missing from in-kind side. This includes not only chess, but confluence etc. For example for EMU development, we would have a much easier job if the configuration and version numbering of EPICS modules were documented in Catania.

## Slide 7: Organization
Address commissioning as one cross-division “core team” with clearly defined roles and responsibilities. Engage proactively with the rest of the commissioning team to ensure better coordination of activities
“Installation and commissioning team” in hardware and integration group.
Effective teamwork with high level of commitments.
Reinforce
Improve
Clarity in role and responsibility distribution (Interlock system, Power supplies, electrical connection and installation, racks etc.)
Many valuable experiences and information are lost when key system owners leave.
Notes: - Installation and commissioning team was a very good initiative in hwi team. During the isrc commissioning, we realized that control support during commissioning is not a one-man job but it requires a team. We still have one person as integration coordinator per section but a group of people as installation and commissioning team are supporting him.
Well, this is obvious for everyone. We had many challenges and issues and without a good teamwork and commitments, we wouldn’t have stable beam ever.
There are still many areas that the boundaries between responsibilities are not clearly defined. As an example for interlock system, after vacuum gate valve incident, we realize that there is really no one responsible for it. Power supplies configuration, electrical installation and connections, racks etc.
There were many key persons who were system owners and we don’t have them now. This is a history and experience that being lost completely. If it combined with inappropriate system tests and verification (FAT and SAT) then it means that 1.we don’t have history and 2. there is no reference or base point so the next person should almost start from ground and build the puzzles. One way of mitigating this risk is to choose at least employees as system owner instead of consultants. Oystein and William were both consultant!

## Slide 8: Planning
Define objectives, scopes and deliverables well in advance and revise regularly based on compiled data from everyone involved. Inappropriate planning and schedule pressure would lead to “prototype systems” that are expensive to operate and maintain.
Reinforce
Improve
Instant decisions and planning in daily operation meetings.
More realistic high level commissioning plan. Move from open loop planning to closed loop with the feedback of stakeholders input.
If critical infrastructure activities are significantly delayed, the commissioning project should be re-planned accordingly.
Establish a prioritized list for control systems early in order to allow for correct planning of work.
AD-ICS program management forum
Agile and flexible approach to enable rapidly changing priorities
Notes: - The AD-ICS forum was a very big step forward. It reduces the burden on integrators shoulders by defining the priorities and schedules between stakeholders themselves instead of at integrators or WP level.
This was the pros of daily operation meeting as all stakeholders are gather together in the same room which made the prioritization easier BUT …
There were many instant decisions and planning made within 15 minutes meeting. This meeting was intended to follow-up the activities performed in last day and plan of activities for the current day. Longer than one-day planning should be made in appropriate forum including just stakeholders involved.

## Slide 9: Preparation and execution
Ensure that all system tests and integration tests are carried out completely prior to starting commissioning activity. This would help system owners to find faults and bugs before which leads to less incidents and system changes.
Reinforce
Improve
Inadequate system/integration tests caused many unexpected problems.
Many signs were observed and ignored prior to incidents. (Vacuum gate valve, Coils PS)
Hardware change -> control system redesign -> Cost and time (Chopper, Steerers PS)
Good examples: Vacuum and Personal Safety System

## Slide 10: Administration
Ensure that system documentations are well addressed in planning and time estimation.
Formal procedure for mask/change interlock system.
Good preparation for ISrc-LEBT SRR.
Reinforce
Improve
More established procedure and formality in handing over the systems to operation.
Many of documentations were missing or out-dated.

## Slide 11: Interfaces
Issues should be reported to relevant stakeholders and only after initial analysis from operators. This requires good tools and services provided to operators.
Good request channel stablished recently ( operator -> stakeholder -> integrator)
Reinforce
Improve
Operator’s involvement in OPI designs and get in touch directly with software group.
Many incoming calls from LCR that were irrelevant to integration.

## Slide 12: Summary
 | Issue | Comments
1. | Planning and coordination | The high level ISrc-LEBT commissioning planning was not adjusted based on reality resulted in higher cost, effort and time.
2. | Preparation and execution | System tests were not carried out completely which caused many double works and prototype systems.
3. | Clear definition of roles and responsibilities | The boundary of system ownerships were not clearly defined that caused some overlap in activities.
Top 3 Issues that we need to improve