## Slide 1: SPL Mock-up: Thermo-Mechanical Results of the First Test
Rossana Bonomi
Rossana.Bonomi@cern.ch
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013

## Slide 2: Outline
Intro
SPL Mock-up Test: Motivations
Test Set-up
Preliminary Results
Improvements / Next steps
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013

## Slide 3: The SPL Short Cryomodule
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Courtesy of CNRS
Notes: Short recall on the SPL SCM =
Dropped as a project by cern but kept as a R&D study
SC linac high power for neutrino factory and neutron science
Representative of half high-beta cryomodule
Some critical parts for what concerns the thermal management have to be tested before construction ..

## Slide 4: SPL Short Cryomodule Status
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
SM18 at CERN - Clean room upgrade (class 10)
Assembly tooling
Courtesy of CNRS
Courtesy of O. Capatina
First SC RF 5-cell cavity from RI
Courtesy of V. Parma
2014
2015
Notes: SPL Project status
Upgrades of infrastructure at cern for assembly/test
Assembly tooling being study by CNRS in the framework of the french collaboration
First cavity in Nb received recently (Nuria+Nacho)
Overall schedule:
Clean room ready in 2014
Start production of tooling
Cavity testing in 2014
Cavity assembly beginning 2015
Cryomodule assembly end of 2015

## Slide 5: SPL Mock-up Motivation
Need validation of:
  Cavity supporting system
  Assembly realignment of cold mass via vessel interface
  Alignment measuring device (OWPM)
  Thermal contractions
  DWT active cooling
..a mock-up has been
built for this testing purposes
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Notes: Critical parts to be tested:
Supporting scheme
Alignment system
Concerning the thermo-mech performance

## Slide 6: Principal Components
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Cold mass filled with LN2
Double-walled tubes cooled by GN2
Intercavity supports (spherical bearings + sliding cylinders)
Vacuum vessel
LN2 dewar, vacuum pumps
Acquisition systems
Notes: List of principal components with external view and internal schematics ..

## Slide 7: Instrumentation
Thermal:
  Temperature sensors (Pt100)
  Heaters (65 W)
  Level gauges (Pt100)
Mechanical:
  Displacement sensors
  Strain gauges
  Targets for laser tracker
Notes: Instrumentation list:
Thermal
Mechanical
Levels LN2

## Slide 8: Control / Safety Devices
GN2 flow rate varied via flow-controllers (30 l/min max) at the gas line outlet
Heating resistance on external DWT flanges controlled via rheostats manually
LN2 flow rate controlled manually and independently via on-off valves
Safety valves on inlet-outlet lines, cold mass
Relief plate on vacuum vessel
Non-return valve on vent line
Notes: Components for control:
Flow-controllers for GN2
Heaters manual for DWT flanges
Safety devices

## Slide 9: Test Set-up
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013

## Slide 10: Test Performed
Approximatively 3 weeks of testing between October-November 2013
Various configurations of cooling conditions tested
No RF power
Temperatures, stresses and displacements were recorded continuously
(1 Hz rate)
Test Program as of 10/2013
Notes: What we did
Acquisition systems recorded at 1 Hz
And the program agreed before starting the test in october

## Slide 11: Results Temperatures Evolution
Temperature [ºC]
Cumulative time [s]
~ 3 hours
50 degrees
Measured
31/10/2013
23 temperature sensors
+ 4 level sensors
Example of cold mass filling
Notes: Just an example of temperature evolution in time
Filling of cavities, gas coolind of coupler, ..

## Slide 12: Results Intercavity Supports
T8
T9
T12
T13
T14
T10
Numeric Estimation
Measured
31/10/2013
Agreement between estimations and measures
As expected, no thermal difformity
Cooling rates comparable to other components
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Notes: Numerical estimations vs measurements
Agreement in the sense that no difformity is measured
And cooling rates are comparable to those of other components

## Slide 13: Results Double-walled Tube
Temperature profiles of DWT
Measured
30/10/2013
Good agreement between estimations (semi-analytical model) and measures
Temperature difference is within expectations
No gas cooling
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
300 mg/s gas cooling
(220K inlet temp)
Notes: Despite the difficulty of finding steady conditions during test,
We have very good agreement btw analytical and measurements,
For both cooled and not cooled cases\
We needed to make few assumptions on the inlet gas temperature based on the other registered temperatures

## Slide 14: Results Heat Loads Estimation
* C. Maglioni, V. Parma’s technical note: “Assessment of static heat loads in the LHC arc, from the commissioning of sector 7-8”, LHC Project Note 409, 2008 (VV TS 1.7 W/m2 - TS  CM 0.1 W/m2)
Subassembly | Heat load @ 77 K [W] | Analsyis details | Comments
Double-walled tubes (2x) D = 100 mm L = 300 mm 1.5 and 2 mm thick walls Copper on stainless steel | 21.4 / 1.4 | Conduction through wall (300-77 K) No gas cooling / With gas cooling (18 l/min) No RF power | Semi-analytical
 | 0.2 | Radiation from 300K DWTs surfaces (blackbodies) View factor 0.026 | Analytical
Lines Gas and liquid lines Inlet-outlet DN = 20 mm Various lengths Stainless steel | 0.3 | Conduction through lines (300-77 K) | Analytical
Vacuum vessel | 6 | Radiation vacuum vessel – cold mass (MLI) Rescaled from LHC measurements* 3.5 m2 cold mass | Analytical
Instrumentation cables | < 2 | Educated guess | 
TOT for SPL Mock-up [W] | 30 / 10 | No gas cooling / With gas cooling | 
Conduction
22 / 2 W
Notes: Estimation from analytical, LHC measurements etc
Biggest contribution is due to conduction when no DWT cooling !!
Great difference btw cool/no cool of couplers => necessary active cooling

## Slide 15: Results Mechanical Measurements
No constraints appearing on ICSs during cool-down
Max displacement between cold masses 4 mm as expected
Max bending stress measured on coupler 20 MPa correspondent to expected friction in ICSs
Work in progress ..
(all mechanical results seem to be as expected)
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013

## Slide 16: Summary
Validation of:
  Cavity supporting system
  Assembly-realignment of cavities via vessel interface
  Alignment measuring device (OWPM)
  Thermal contractions
  DWT active cooling
..Further testing is needed !
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Notes: Cosa e’ stato fatto e cosa no

## Slide 17: Improvements / Next Steps
Latest improvements put in place
  GN2 line
    Smaller, better insulated line
    Temperature sensor on gas inlet line
    Second dewar to extract colder GN2
  Targets
    Further cleaning to avoid condensing gases
  Vacuum leaks fixed
Other possible improvements / modif
  Separator inside the cryostat
  Flowmeters on vent line for accurate measurement of static loads
  ..
..Possible mitigations to experienced problems
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013
Notes: Cosa stiamo cambiando
Cosi prevediamo di aggiungere in futuro (reservoir? OWPM?)

## Slide 18
Thank you
Tack för din uppmärksamhet !
Acknowledgements
A. Vande Craen, W. Zak, M. Souchet,
A. Guimet, J.B. Deschamps, A. Bastard, P. Coelho
M. Guinchard + team
L. Dufay, F. Girardot
C. Charrondiere, E. Rasoaseheno
C. Parente, D. Gonnard
J. Bjorklund
T. Koettig
S. Le Naour, D. Duarte
E. Montesinos, R. Wegner
Bonomi, ESS Retreat Meeting, Lund, 10-11/12/2013

## Slide 20: LHC Multi layer insulation (MLI)
Features:
1 blanket (10 reflective layers) on cold masses (1.9 K)
2 blankets (15 reflective layers each) on Thermal Shields (50-65 K)
Reflective layer: double aluminized polyester film
Spacer: polyester net
Stitched Velcro™ fasteners for rapid mounting and quality closing
Interleaved reflectors and spacers
1 blanket on CM, 2 on thermal shield
Velcro™ fasteners
Blanket manufacturing

## Slide 21: Thermodynamic efficiency of DWT gas cooling
(Figure from: « An Introduction to Cryogenics », Ph.Lebrun, CERN/AT 2007-1)
He refrigeration He Liquefaction
Electrical power for liquefaction of 1 g/s helium: 6200 Wel
Carnot COP @ 4.5 K: 66 Wel/Wth
1 g/s liquid helium is equivalent to 100 Wth @ 4.5 K *
* U. Wagner s presentation: http://cdsweb.cern.ch/record/808372/files/p295.pdf