## Slide 2: Accelerator ODHDS Preliminary Design
PRESENTED BY Donya Daryadel

## Slide 3: Agenda
Presenting distribution of ODH monitors in the tunnel
Typical installation for ODH sampling pipe
Alarm activation matrix
Reviewing the data extracted from CFD
Propagation, detection and alarm time

## Slide 4
1
Presenting distribution of ODH monitors in the tunnel

## Slide 5: CRYOMODULES OVERVIEW IN THE ACCELERATOR TUNNEL
The Accelerator ODH Detection System is designed to cover the potential asphyxiant gas leak points of cryogenic system located in the Superconducting LINAC (SCL) tunnel.
The SCL contains 30 elliptical cryomodules, whereas 9 are medium-beta and 21 high-beta, and 13 spoke cryomodules.

## Slide 6: Site visit with cryo expert

## Slide 7: Site visit with cryo expert

## Slide 8: SAMPLING POINTS DISTRIBUTION IN THE TUNNEL
The distance from the end box to end of the last cryomodule is about 310m.
We covered this length by 13 sampling points.
If we divide 310 to 13 we reach 23.8m.
We tried to distribute the sampling point evenly in the tunnel, considering the location of the stubs and the leak points and length of the sampling pipes.
Based on our current design the distance between our sampling points in the tunnel are between 17~27m with the average of 24.6m.

## Slide 9: SAMPLING POINTS DISTRIBUTION IN THE TUNNEL
Sampling point distribution relative to the location of the cryomodules and stub no.are as below table:
Stub no. | Nearest Cryomodule no. | Nearest cryomodule with sampling point | Distance (m)
120 | SPK2-SPK3 | SPK3 | 12.8
130 | SPK6-SPK7 | SPK7 | 17
140 | SPK10-SPK11 | -- | --
150 | SPK13-MBL1 | SPK13 | 25.7
160 | MBL2-MBL3 | MBL3 | 20.7
170 | MBL4-MBL5 | -- | --
180 | MBL6-MBL7 | MBL6 | 27.4
190 | MBL8-MBL9 | MBL9 | 23.7
200 | HBL1-HBL2 | -- | --
210 | HBL3-HBL4 | HBL3 | 27.4
Stub no. | Nearest Cryomodule no. | Nearest cryomodule with sampling point | Distance (m)
220 | HBL5-HBL6 | HBL6 | 24.5
230 | HBL7-HBL8 | -- | --
240 | HBL9-HBL10 | HBL9 | 26.6
250 | HBL11-HBL12 | HBL12 | 24.4
260 | HBL13-HBL14 | -- | --
270 | HBL15-HBL16 | HBL15 | 26.8
280 | HBL17-HBL18 | HBL18 | 24.2
290 | HBL19-HBL20 | -- | --
300 | HBL21 | HBL21 | 26.9

## Slide 10: SPOKE CRYOMODULES
The Spoke Linac (SPK) is the first stage of the SCL.
It consists of the 13 spoke cryomodules.
There are in total three sampling points, which are positioned by:
  Spoke 3
  Spoke 7
  Spoke 13
25.7m
17m
12.8m

## Slide 11: MBL CRYOMODULES
It consists of the 9 elliptical cryomodules.
There are in total three sampling points, which are positioned by:
  MBL 3
  MBL 6
  MBL 9
23.7m
27.4m
20.7m

## Slide 12: HBL CRYOMODULES
It consists of the 21 elliptical cryomodules.
There are in total 7 sampling points, which are positioned by:
  HBL 3, 6, 9, 12, 15, 18, 21
26.6m
24.5m
27.4m

## Slide 13: HBL CRYOMODULES
24.2m
26.5m
24.4m

## Slide 14: HBL CRYOMODULES
26.9m

## Slide 15: Section views

## Slide 16: ODH monitor in G02

## Slide 17
2
Typical installation of ODH sampling pipe

## Slide 18: Typical installation for ODH sampling pipe
ODH sampling point

## Slide 19: Typical installation for ODH sampling pipe
Pipe route on the wall in G01

## Slide 20: Typical installation for ODH sampling pipe
Exhaust air pipe

## Slide 21: Typical installation for ODH sampling pipe
Stub in G01

## Slide 22: Typical installation for ODH sampling pipe
Pipe route on the roof in G01

## Slide 23: Typical installation for ODH sampling pipe
ODH monitor in G02

## Slide 24: Typical installation for ODH sampling pipe
Pipe route in G02

## Slide 25: Typical installation for ODH sampling pipe
Stub in G02

## Slide 26
3
Alarm activation matrix

## Slide 27: Alarm activation matrix

## Slide 28
4
Reviewing the data extracted from CFD

## Slide 29: Accelerator tunnel
CFD simulations
Scenario 2 (2.4 kg.s-1 during 2 s) – rupture of the vacuum vessel of a High-β
Nearest exit from the A2T
Discharge point
A
C
B
Ventilation ON
25 200 m3/h
Acknowledgement : E.LUNDH

## Slide 30
Ventilation ON
25 200 m3/h
A
Acknowledgement : E.LUNDH

## Slide 31
B
Ventilation ON
25 200 m3/h
Acknowledgement : E.LUNDH
18%
10s
Propagation time

## Slide 32
5
Propagation, detection and alarm time

## Slide 33: Propagation, detection and alarm time
Review committee recommendation 2016
~10s
~7s
<1 s
~ 18 s
Rough estimation

## Slide 34: Finish presentation

## Slide 36: Spoke 3 sampling point layout

## Slide 37: Spoke 7 sampling point layout

## Slide 38: Spoke 13 sampling point layout

## Slide 39: MBL 3 sampling point layout

## Slide 40: MBL 6 sampling point layout

## Slide 41: MBL 9 sampling point layout

## Slide 42: HBL 3 sampling point layout

## Slide 43: HBL 6 sampling point layout

## Slide 44: HBL 9 sampling point layout

## Slide 45: HBL 12 sampling point layout

## Slide 46: HBL 15 sampling point layout

## Slide 47: HBL 18 sampling point layout

## Slide 48: HBL 21 sampling point layout