## Slide 2: SE Integration and integration infrastructure
Solutions and labs
Experiment Control and Data Curation (ECDC)
Anders Pettersson

## Slide 3: NICOS
  Instrument cabin
  User and Expert interface
  Qt based
  Extensible and customizable
All devices shall be available in NICOS
  Scripting
  Python CLI
  Plotting live data

## Slide 4: EPICS
EPICS - Experimental Physics and Industrial Control System
  EPICS is the signal layer backbone at ESS
  Every remote controlled signal or data need to be available as an EPICS PV (Process Variable)
  All SE hardware is integrated into EPICS
  ICS WP12 provide integration working close with ECDC
  ECDC priorities NSS integration tasks
  All data will be timestamped in EPICS
Integrated Control Systems Division - ICS WP12
Notes: Open source facility control system/Scada system used at large research facilities (radio telescope array, telescopes, synchrotrons, Xfel etc).

## Slide 5: EPICS
From SE perspective
CS-Studio Phoebus -> Engineering Interface (mainly SE team)
Troubleshooting/development interface
Archiver –> long term SE monitoring
Not the interface for the User
Potentially providing device hardware configuration parameters not exposed to User.
Will not provide scripting
CS-Studio Phoebus GUI, Archiver

## Slide 6: Overview SE integration
From hardware to User interface
EPICS
Octopy
NICOS
EPICS
forwarder
Kafka
Filewriter
NeXus/HDF5
ESS Timing network
EPICS Process Variables (PV)
Technical Network
SEE
SE System
SEE
Local IPC
User interface
Notes: Exposeing signals on EPICS enable access on ESS controls infrastructure

## Slide 7
(mention octopy..)
Different solutions
Same User Experience
2

## Slide 8: Different solutions Same User Experience
EPICS
  Standard devices are straightforward in EPICS
  Robust
  GUI, Archiver, Save and Restore
  Some community integrations available
Use case: EPICS for standard systems

## Slide 9: Different solutions Same User Experience
  Not straightforward with EPICS
  Labview not supported by ICS
  Labview ”EPICS” not ”adviced” by ICS
  ICS only supports Linux machines (win required)
  ”Normal” complexity with Octopy
  Octopy python based, runnable on most systems
Use case: Octopy for device requiring a DLL (potentiostat)
Notes: Octopy provide a solution where EPICS is limited

## Slide 10: Different solutions Same User Experience
  Octopy provide SE with a toolbox for SE low level complexity
  Configurations can be changed dynamically enabling modularity
  Python libraries can be used
  Python scripts can be added in a modular way
  SE staff can code (low threshold)
Use case: Octopy Development systems Orange Cryostat, Rig1, LS336 Tctrl calib

## Slide 11: Different solutions Same User Experience
  Timestamping for SE (”raw” signals)
  PLC (Beckhoff) synchronize to ESS time through PTP
  Standard MQTT library is used for PLC to push data to Octopy -> EPICS
  The Provides solution for timeresolution 10-100us and sample rate 1-10ks/s
Use case: Higher timestamping resolution

## Slide 12: Different solutions Same User Experience
  Translate a SECoP device to EPICS
  Develop a ESS SE system for SECoP
Use case: Octopy for SECoP Devices
Network

## Slide 13: Integrated devices
Lakeshore 155 I-V Source
Lesker kjlc392 vaacuum gauge
Schlumberger Freq Resp Analyzer
AMI 1700 LN2/LHE Level Instrument
Burster Resistance Decade 1427
ESI Pressure Gauge monitor
Flir camera
Kepco BOP50-2m Power Supply
LakeShore 224 T Monitor
LakeShore 336 T Controller
Vinci HP syringe pump
GE Pace 5000 P Calibration system
Huginn Peltier-Based T Control
Julabo F25 HL
NE1002x Syringe Pump
NE1600 Syringe Pump
NE9000 Peristaltic Pump
Camera Alignment System (CAS)
Beckhoff as toolbox
Knauer Azura P 6.1L HPLC

## Slide 14: Thoughts on integration
An available SE ”expert” is essential for the integration
Some basic devices integrated
Octopy completes integration toolbox for SE
(current) Infrastructure mostly in place (finally) in SE labs
YMIR will allow closer to ”real deal” testing
Too few SE systems to integrate. Essential for develop modularity, logic, complexity
Too few ongoing projects, ICS resources very limited but still underutilised by SE
Still some struggles with infrastructure
Good things and challenges..

## Slide 15
B02 Controls lab
YMIR instrument
.

## Slide 17: YMIR beamline in ESS B02 Facility
  YMIR:
  Physical Instrument without neutrons
  Provide latest instrument control system
  Planned Instrument network infrastructure
  Utilities for SE
  Soldering station
  Cross group collaboration workplace
  Easy access promoting interactions with instrument teams, tech teams,
  Demonstrator
Collaborative lab space for SE, ECDC, MC&A, Chopper, instr etc

## Slide 18: YMIR beamline
Current devices
Laser beam + detector readout
Running Mini-chopper
SE XYZ scanning system
Timestamping system (SE, ICS, MC&A)
Non-magnetic floor
SE K-mount
Light tomography

## Slide 19: YMIR beamline
Testrun equipment as a SAT, integration SAT
Test new developments ”offline”
Test arriving equipment in non supervised zone
Demonstrate/test complete control chain for SE
Strengthen collaboration cross teams
SE comtrols infrastructure development
  SE plug and play
  Timestamping
  TTL synch
  ….
For Sample Environment

## Slide 20: Summary
  Complementary integration solutions
  One user interface
  EPICS/NICOS UI available for SE
  Octopy used by SE to build complex SES
  Octopy provide local flexibility
  YMIR help drive SE controls development
  B02+E03 etc big step towards final SE controls structure
  Beckhoff PLC + Octopy provide standard for raw signals, hi-res timestamping and motion

## Slide 21: Thank You for listening!