## Slide 2: Overview of the Target Station PSS (TS PSS)
Concept of Operations and Interfaces
PRESENTED BY Afshin farshidfar

## Slide 3: Agenda
1 Target Station Utility Block
2 TS PSS Controlled Area and Main Functions
3 System Interfaces
4 Operational Activities

## Slide 4
Target Station Utility Block
1

## Slide 5: Target Station Utility Block

## Slide 6: Target Station Utility Block
Target Basement
Bunker Floor
Target Basement Floor
LSS

## Slide 7
TS PSS Controlled Area and Main Functions
2

## Slide 8: TS PSS Controlled Area
Level 091(Target Basement)
 | Designated radiation areas |  |  |  | 
Definition |  |  |  |  | 
Criteria/Area classification | Green Supervised Area | Blue Controlled Area | Yellow Controlled Area | Red Controlled Area | Magenta Prohibited Area
Potential annual effective dose | <6 mSv | >6 mSv | >6 mSv | >6 mSv | -
Ambient equivalent dose rate | <3 µSv/h | <25 µSv/h | <2.5 mSv/h | <100 mSv/h | >100 mSv/h
Controls |  |  |  |  | 
Access control | Access control | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Access Prohibited
Radwork permit | Required | Required | Required | Required | 

## Slide 9: TS PSS Controlled Area
Level 103
 | Designated radiation areas |  |  |  | 
Definition |  |  |  |  | 
Criteria/Area classification | Green Supervised Area | Blue Controlled Area | Yellow Controlled Area | Red Controlled Area | Magenta Prohibited Area
Potential annual effective dose | <6 mSv | >6 mSv | >6 mSv | >6 mSv | -
Ambient equivalent dose rate | <3 µSv/h | <25 µSv/h | <2.5 mSv/h | <100 mSv/h | >100 mSv/h
Controls |  |  |  |  | 
Access control | Access control | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Access Prohibited
Radwork permit | Required | Required | Required | Required | 

## Slide 10: TS PSS Controlled Area
Level 115
 | Designated radiation areas |  |  |  | 
Definition |  |  |  |  | 
Criteria/Area classification | Green Supervised Area | Blue Controlled Area | Yellow Controlled Area | Red Controlled Area | Magenta Prohibited Area
Potential annual effective dose | <6 mSv | >6 mSv | >6 mSv | >6 mSv | -
Ambient equivalent dose rate | <3 µSv/h | <25 µSv/h | <2.5 mSv/h | <100 mSv/h | >100 mSv/h
Controls |  |  |  |  | 
Access control | Access control | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Personal dose limits used for access, restricted access | Access Prohibited
Radwork permit | Required | Required | Required | Required | 

## Slide 11: TS PSS
Overview
Level125
Level115
Level103
Level091
TS PSS has two HMIs:
An integrated ACC, Target and Bunker HMI in MCR(MCR PSS HMI)
A dedicated HMI in high bay

## Slide 12: Main Functions
The TS PSS provides the following main functions:
TS PSS prevents access to TS PSS controlled area, by locking the access doors to the TS PSS controlled area in a closed position when the BoT is allowed.
TS PSS prevents inadvertent energization of the bending magnets if the TS PSS controlled area is not searched and locked.
TS PSS requests Accelerator PSS (ACC PSS) to switch off the proton beam, if an intrusion to TS PSS controlled area is detected when the BoT is allowed,
TS PSS requests ACC PSS to switch off the proton beam, if an ESOB is pressed in TS PSS controlled area when the BoT is allowed,
TS PSS prevents access to the TS PSS controlled area in the target basement if the light shutters are not closed
TS PSS prevents inadvertent opening of the light shutters if the TS PSS controlled area in the target basement is not searched and locked
TS PSS requests ACC PSS to switch off the proton beam if it receives a high radiation alarm or major fault signal from the designated radiation monitors installed in D02.120.4014 and D02.115.4005 when the BoT is allowed.

## Slide 13
System Interfaces
3

## Slide 14: Equipment Under Control
Proton Beam Actuators
The TS PSS interfaces with the proton beam actuators of ACC PSS to stop proton beam generation in certain hazardous scenarios.
The communication between ACC PSS and TS PSS is realised through Nexus PSS.
The TS PSS shall inform the Nexus PSS on the TS PSS Ready for BoT status.
The TS PSS shall receive feedback on the following:
      BoT Status
      Isrc HVPS status

## Slide 15: Equipment Under Control
Proton Beam Actuators
The controlled area is ready for operation if:
TSPSS_SIF1, 2, 3, and 5 are reset
All zone gates (including lead bunker door) are closed and error free
The controlled area is searched and locked
No SIS diagnostic alarms
TSPSS_SIF1: Emergency Stop Buttons
TSPSS_SIF2: E-Exit doors interlock
TSPSS_SIF3: Access Doors Interlock
TSPSS_SIF5: High Radiation Alarm

## Slide 16: Equipment Under Control
Proton Beam Actuators

## Slide 17: Equipment Under Control
Connection Cell Shielding Door

## Slide 18: Equipment Under Control
Sliding Concrete Doors

## Slide 19: Equipment Under Control
Emergency Exit Doors

## Slide 20: Equipment Under Control
Solenoid
Key Exch. Unit
TS PSS
Bunker
PSS
LSS
Status
Permit
Status
Permit
EK
Closed
Closed
Disabled
Disabled
Prevent access to TS PSS controlled area in the Target basement when the Light Shutters are not closed,
Prevent inadvertent opening of the Light Shutters when access to the Target basement is allowed
TS PSS Functions
Light Shutter System

## Slide 21: Interfaces
  The TS PSS contributes to the shielding configuration management of removable shielding blocks.
  Lifting the shielding blocks requires the use of a crane.
Removable Shielding Blocks

## Slide 22: Interfaces
TS PSS interfaces with the door through position monitoring switches to ensure that the lead bunker sliding door is closed before allowing the BoT.
If the door is detected open after D02.115.4003 is searched and locked, an alarm shall appear on TS PSS HMI and OPI.
Lead Bunker Shielding Door

## Slide 23: Interface Points
Signal name | Signal status | NO contact status (Relay) | ACC PSS permit
Radiation alarm | TRUE (the radiation level is below set threshold) | Closed | Enabled
 | FALSE (the radiation level is above set threshold) | Open | Disabled
Major fault | TRUE (there is no fault in AMM) | Closed | Enabled
 | FALSE (the AMM is faulty) | Open | Disabled
Radiation Monitors

## Slide 24: Other Interfaces
Blue Lights
Indicate that ionizing radiation is imminent or exists.
Turn ON when the beam on target is ALLOWED.
Installed in the controlled area.
Gas Detection System
ODH monitors measure and display the O2 level.
ODH alarm devices alarm in case of oxygen deficiency.
The message display above the access door to D02.115.4003 will display “ACCESS PROHIBITED” if a ODH evacuation alarm is triggered in the room.

## Slide 25
Operational Activities
4

## Slide 26: TS PSS Operational Activities
Principles of Operation
Prior to enabling TS PSS permit to allow the BoT:
    Trained operators carry out a formalised search in TS PSS controlled area,
    TS PSS locks the access points to TS PSS controlled area.
Notes: TS PSS protects workers by ensuring a safe state of TS PSS controlled area when it is accessible, as well as ensuring that no one is left inside the TS PSS controlled area when it is unsafe

## Slide 27: TS PSS Operational Activities
Principles of Operation
Prior to granting access to TS PSS controlled area:
  The operator stops the proton beam on the target through the control system,
The cool down time has to be elapsed before TS PSS allows access to the PSS controlled area,
  The operator closes the light shutters through the control system if access to the target basement is required,
  Upon initiating access to TS PSS controlled area, TS PSS interlocks the bending magnets, to prevent their inadvertent energisation. The bending magnets are secured against re-energisation until the TS PSS controlled area is searched and locked,
  Upon initiating access to the TS PSS controlled area in the target basement TS PSS interlocks the light shutters, to prevent their inadvertent operation. The light shutters are interlocked in the closed position until the TS PSS controlled area in the target basement is searched and locked,

## Slide 28: Target Station PSS Mode Transitions
Access
Mode
Beam ON Mode
Alarm Mode
Transition
Mode
PB Interlock Mode

## Slide 29: TS PSS Modes of Operations
Access
Mode
Beam ON Mode
Transition
Mode
TS PSS Ready for BoT :disabled
BoT is Allowed
Formalised Search can be carried out only in this mode
Feedback From Nexus
Blue Lights: OFF
Access doors: can be unlocked
Shielding blocks: can be unlocked
Light Shutters: can be interlocked
Search: broken upon first access
TS PSS Ready for BoT: can be enabled
Blue Lights: OFF
Access doors: closed and locked
Shielding blocks: locked
Light Shutters: not interlocked
Search is completed
TS PSS Ready for BoT: enabled
Blue Lights: ON
Access doors: closed and locked
Shielding blocks: locked
Light Shutters: not interlocked
Search is completed
Notes: Mode
Description
Access
This is the normal access mode of the system
BoT ON
In BoT ON mode, all prerequisite of allowing BoT by ACC PSS are provided.
Transition
The Transition mode is used when TS PSS transitions from BoT ON to Access mode, and vice versa. In this mode TS PSS issues all permits necessary for the Target Station user(s) to be able to initiate beam to Target and wait for other conditions that need to be received by ACC PSS to enable permit to allow BoT.

## Slide 30: TS PSS Modes of Operations
TS PSS Ready for BoT is disabled
Alarm Mode
TSPSS_SIF2(Intrusion)
TSPSS_SIF1(ESOB)
In any TS PSS mode
In Beam ON or Transition modes
Alarm Mode
PB actuator feedback error
In Access mode
Bad key combination
SIS startup
Access
Mode
TSPSS_SIF3(Intrusion)
TSPSS_SIF1 is reset
TSPSS_SIF2 is reset
PB is interlocked OFF the target
No PB feedback error
System is not in startup mode
Search is broken for certain triggers

## Slide 31: TS PSS Modes of Operations
Alarm Mode
PB Interlock Mode
Beam ON Mode
TSPSS_SIF5(High Radiation)
PB Interlock Mode
TSPSS_SIF5 is reset
TS PSS Ready for BoT is disabled
Search is not broken
Transition
Mode
TSPSS_SIF1(ESOB)
SIS startup
PB is interlocked OFF the target

## Slide 32: TS PSS key Exchange System
Integrated ACC – Target - Bunker PSS key exchange unit #1 (MCR)
Target PSS key exchange unit #2 and HMI

## Slide 33: Target PSS Key Exchange System
Spare
SCMK7
LVL103
SCMK5
LVL115
SCMK4
LVL115
SCMK3
BOT
OVK
S
S
S
S
S
S
BOT MK
SLOT 12
SLOT 14
SLOT 16
SLOT 18
SLOT 20
SLOT 13
SLOT 15
SLOT 17
SLOT 19
BOT MK
BOT MK is locked in slot 14 until BoT is permitted
BOT MK not in Slot 12 = Bending Magnets are interlocked
BOT OVK is managed by RP team. The solenoid is removed through HMI with RP credentials
T AVK is managed by RP team. The solenoid is removed through HMI with RP credentials
S
Permit for Beam On Target
Unit #1
(ACC - Target – Bunker Scope)
The Solenoid on slot 6 is removed only when all Light Shutters (LS) are closed. The LS are interlocked in the closed position when EK3 is not in the home position.
NWB AK
SEB AK
T AK
NWB AVK
SEB AVK
T AVK
S
T AK is locked in Slot 16 until cool down time is elapsed
Unit #2
SLOT 1
SLOT 2
SLOT 3
SLOT 4
SLOT 5
SLOT 6
SLOT 7
SLOT 8
SLOT 9
SLOT 10
SLOT 11
SLOT 12
SLOT 13
SLOT 14
S
Connection Cell Shielding Block
Hatch Door Slab1 in HB
D02.115.4001
D02.115.4003
D02.103.4003
D02.091.4003
TS AK
TS SCMK
EK1-CCELL
EK2-LVL115
EK3-LVL103
EK3-LVL091
Hatch Door Slab1 in 115.4003 Floor
Hatch Door Slab2 in 115.4003 Floor
Hatch Door Slab1 in 103.4003 Floor
Hatch Door Slab2 in 103.4003 Floor
TS SCMK
CCELL
SCMK1
HBAY
SCMK2
LVL103
SCMK6
Beam ON Mode
Transition
Mode
Access
Mode
Access Prohibited
Access Prohibited
Access Prohibited
Access Prohibited
Access Allowed
Access Allowed
Access Allowed
Access Allowed
T AK
EK4
EK3
EK2
EK1
TS
SCMK
TSCMK1
TSCMK2
TSCMK3
TSCMK4
TSCMK5
TSCMK6

## Slide 34: TS PSS Key Exchange System
T AK
Access Veto Procedure
TAK is locked in slot 2 until TAVK is back
T AVK is managed by RP team. The solenoid is removed through HMI with RP credentials
BOT
OVK
S
S
S
S
S
S
BOT MK
SLOT 12
SLOT 16
SLOT 18
SLOT 20
SLOT 13
SLOT 15
SLOT 17
SLOT 19
BOT MK
S
Permit for Beam On Target
Unit #1
(ACC - Target – Bunker Scope)
NWB AK
SEB AK
NWB AVK
SEB AVK
T AVK
S
Handled by RP
T AK

## Slide 35: Formalised Search
TS PSS Search Zones
LVL091
LVL103
LVL115
Zone2
Zone1
Zone3
Zone5
Zone6
Zone7
Zone1
Zone4
Notes: A Formalised Search is carried out by pressing search buttons which are distributed in a way that requires the search team to inspect all corners of the search area.
The search buttons are to be pressed in a predetermined sequence, with a time delay between pressing two buttons.
PSS controlled area is divided in 6 search zones.
A Formalised Search is to be performed by designated trained personnel, which is called the search team, when TS PSS is in Access mode.
The minimum number of personnel required in a Search Team is defined based on complexity of search zones

## Slide 36: Formalised Search
Target basement
Zone No. | Search Time
1, 2, 3 | 3 min
4 | 3 min search + 4 min door closing

## Slide 37: Formalised Search
Zone1
Zone2
Zone3
Zone1
Zone2
Zone3
Zone1
Zone2
Zone3
Target basement
Zone1
Color Code | Definition
 | Searched
 | Not Searched
Zone4
Zone4
Zone4

## Slide 38: Formalised Search
Zone1
Zone2
Zone3
Target basement
Color Code | Definition
 | Searched
 | Not Searched
Searching
Notes: The search can start only in Access mode when the precondition of the search are fulfilled.
Mention the key to start the search
Mention the PA

## Slide 39: Formalised Search
Target basement
Color Code | Definition
 | Searched
 | Not Searched
Searching
TSCMK5
TSCMK6
From LVL103
Sliding concrete door detected closed

## Slide 40: Formalised Search
Level 103 (D02.103.4003)
Zone No. | Search Time
5 | 4 min search + 4 min door closing

## Slide 41: Formalised Search
Level 115(D02.115.4003)
Zone No. | Search Time
6 | 4 min search + 4 min door closing

## Slide 42: Formalised Search
Level 115(D02.115.4003)
An extra search button in this corner?
Is there any concern about the high dose rate in this corner?

## Slide 43: Formalised Search
Formalised Search in D02.115.4003
From High Bay
Color Code | Definition
 | Searched
 | Not Searched
Searching
TSCMK2
Lead bunker door detected closed
TSCMK4
TSCMK5

## Slide 44: Formalised Search
Level 115(Connection Cell)
Zone No. | Search Time
7 | 4 min search + 2 min door closing

## Slide 45: Preparing the Area for Operation
BoT ON Mode
Access
Mode
Transition
Mode
BoTK is locked in slot 2 until ESS PSS BoT permit is enabled
If the area is ready for operation “Ready for BoT” will be enabled
BoT OVK is managed by RP team. The solenoid is removed through HMI with RP credentials
Blue lights turn on and PA broadcast a warning for 120 sec
TS PSS controlled area is searched and locked
All keys are brought back to Unit#2
BOT
OVK
S
S
S
S
S
S
BOT MK
SLOT 12
SLOT 16
SLOT 18
SLOT 20
SLOT 13
SLOT 15
SLOT 17
SLOT 19
BOT MK
S
Permit for Beam On Target
Unit #1
(ACC - Target – Bunker Scope)
NWB AK
SEB AK
T AK
NWB AVK
SEB AVK
T AVK
S
Spare
SCMK7
LVL103
SCMK5
LVL115
SCMK4
LVL115
SCMK3
Unit #2
SLOT 1
SLOT 2
SLOT 3
SLOT 4
SLOT 5
SLOT 6
SLOT 7
SLOT 8
SLOT 9
SLOT 10
SLOT 11
SLOT 12
SLOT 13
SLOT 14
S
TS AK
TS SCMK
EK1-CCELL
EK2-LVL115
EK3-LVL103
EK3-LVL091
TS SCMK
CCELL
SCMK1
HBAY
SCMK2
LVL103
SCMK6
TSPSS_SIF1 and TSPSS_SIF2 are reset
Access Prohibited
Access Allowed
TAK
The controlled area is ready for operation if:
TSPSS_SIF1, 2, 3, and 5 are reset
All zone gates (including lead bunker door) are closed and error free
The controlled area is searched and locked
No SIS diagnostic alarms

## Slide 46: Intervention Activities
LSS operators may need to have access to the target basement for LSS maintenance. During LSS maintenance some of the light shutters might fail to close or may have to stay open while the light shutter maintenance team are in the target basement. PSS has the ability to remove the interlock of one light shutter at a time during LSS maintenance. This will be done true Bunker PSS.

## Slide 47: Thank you for listening!

## Slide 48: Radiation levels(backup)
Radiological Hazards Induced In The Target Utility Block During Normal Operation And Corresponding Radiation Safety Provisions (ESS-2027007)
Area classification design requirements document for the D,E&G buildings (ESS-0057612)

## Slide 49: Formalised Search(Backup)
A formalised search is carried out by pressing search buttons which are distributed in a way that requires the search team to inspect all corners of the search area.
To ensure that the search team performs the formalised search carefully, there is a time delay of 20 seconds between pressing two search buttons in the predefined sequence.
If the button that should be pressed next is pressed within that time, it is not registered as pressed (TSPSS_CON35).
A formalised search is to be performed by at least two designated trained operators, which is called the search team when TS PSS is in Access mode.

## Slide 50: Formalised Search(Backup)
Search prerequisites
Zone No. | Conditions
1 | The door to the ACC emergency escape hatch (DIS606) is closed Emergency exit door to D03 (DIS624) is closed and locked Depending on the search scenario, either of the zone gates DIS603 or DIS604 are closed (see 10.1.2.2) TSPSS_CON37
2 | The annunciator light next to the zone gate DIS603 is lit, i.e. Zone 1 is searched DIS603 is closed TSPSS_CON38
3 | The annunciator light next to the zone gate DIS604 is lit, i.e. Zone 1 is searched DIS604 is closed TSPSS_CON39
4 | The annunciator light next to the zone gates DIS602, and DIS605 are lit, i.e. Zone 2 and Zone 3 are searched DIS602 and DIS605 are closed TSCMK5 and TSCMK6 are returned to KEU#2, i.e. the hatch in the ceiling is closed TSPSS_CON40
5 | TSCMK3, TSCMK4, TSCMK5, and TSCMK6 are returned to KEU#2, i.e. the hatches in the ceiling and the floor are closed. TSPSS_CON41
6 | TSCMK2, TSCMK3, and TSCMK4 are returned to KEU#2, i.e. the hatches in the ceiling and the floor are closed. The lead bunker door is closed and locked TSPSS_CON42
7 | TSCMK2 is returned to KEU#2, i.e. the monolith roof is closed TSPSS_CON43

## Slide 51: Formalised Search (backup)
Search breaking events
Zone No. | Events
1 | The door to the ACC emergency escape hatch (DIS606) is detected open in any TS PSS mode Emergency exit door to D03 (DIS624) is detected open in any TS PSS mode TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode Any of the zone gates (DIS603 or DIS604) are detected open in Access and Alarm modes TSPSS_CON44
2 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode Any of the zone gates (DIS603 or DIS605) are detected open in Access and Alarm modes TSPSS_CON45
3 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode Any of the zone gates (DIS602 or DIS604) are detected open in Access and Alarm modes TSPSS_CON46
4 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode Any of the zone gates (DIS602 or DIS605) are detected open in Access and Alarm modes TSCMK5, or TSCMK6 is removed from KEU#2 TSPSS_CON47
5 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode Any of the zone gates (DIS602 or DIS605) are detected open in Access and Alarm modes Any of TSCMK3, TSCMK4, TSCMK5, and TSCMK6 is removed from KEU#2 TSPSS_CON48
6 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode The lead bunker door is detected open in Access and Alarm modes Any of TSCMK2, TSCMK3, and TSCMK4 is removed from KEU#2 TSPSS_CON49
7 | TS PSS transitions to Alarm mode due to a critical hardware failure Any ESOB in the zone is pressed in any TS PSS mode TSCMK2 is removed from KEU#2 TSPSS_CON50

## Slide 52
Safety Instrumented Functions(SIF)
1

## Slide 53: Safety Instrumented Functions (SIF)
TSPSS_SIF1 – ESOB Interlock
If any emergency switch-off button (ESOB) in the TS PSS controlled area is pressed, and the bending magnets are detected energised (Beam on Target (BoT) allowed) act on the following Equipment Under Control (EUC):
    De-energise Ion Source High Voltage Power Supply (ISrc HVPS),
    Connect the Grounding Relay to earth.
ESOB

## Slide 54: Safety Instrumented Functions (SIF)
TSPSS_SIF1 – ESOB Interlock

## Slide 55: Safety Instrumented Functions (SIF)
LOKIPSS_SIF2 – Emergency Exit Doors Interlock

## Slide 56: Safety Instrumented Functions (SIF)
LOKIPSS_SIF3 – Access Doors Interlock

## Slide 57: Safety Instrumented Functions (SIF)
LOKIPSS_SIF4_1 to 4 –Doors Lock
The safety lock on the access doors on the TS PSS controlled area perimeters, to stay de-energised (locked) in order to prevent and block the access to TS PSS controlled area, when the door Entry Key (EK) is not in ON position on the lock unit

## Slide 58: Safety Instrumented Functions (SIF)
LOKIPSS_SIF5 – High Radiation Interlock