## Slide 2: SIL Assessment for Bunker PSS SIFs
Bunker CDR
PRESENTED BY Jonny Gale & Fan YE

## Slide 3: Agenda
1 Introduction to PSS SIL Assessment
2 Bunker PSS Safety Instrumented Functions (SIFs)
3 Bunker PSS Safety Requirements Specification (SRS)
4 Bunker PSS SIL Assessment Results
5 Bunker PSS Event Tree Analysis

## Slide 4
Introduction to PSS SIL Assessment
1

## Slide 5: PSS SIL Assessment
SIL Determination
  Inputs – Risk Assessments, ConOps
  Outputs – SIL targets for each SIF in terms of PFD/PFH and SIL
SIL Verification
  Inputs – SIL Determination, SIF configurations, Failure Data
  Method – Reliability Block Diagram (RBD), ProSET
  Outputs – SIL Verification results in terms of achieved PFD/PFH and SIL
SRS
SIL Verification
Risk Assessment
SIL Determination
Notes: Point out during presentation that this was already presented in the PDR. We want to give an introduction for new committee members.
The functional safety work we do is the first 4 phases on the lifecycle. So for phase 1 hazard and risk assessment the Risk Assessments for Bunker & TS PSS was used where the SIFs are identified for the radiation and conventional hazardous scenarios. Then we needed to allocate the Bunker & TS PSS SIFs a Safety Integrity Level Target which the SIL determination part for phase 2. And once we’d worked out what the SIFs needs to meet we document this in the Safety Requirements Specification which is phase 3. And then finally once had the SIFs configuration and all of the devices we complete the SIL verification which is phase 4 of the lifecycle.

## Slide 6: SIL Determination and Verification
SIL Determination
  To determine the required SIL target (and reliability target PFD/PFH) for each SIF
  Layers of Protection Analysis (LOPA) used for SIL determination
  Guideline for SIL Assessment for Personnel Safety Systems (ESS-1408224)
SIL Verification
  To verify the proposed SIF design will meet the corresponding SIL (and PFD/PFH) target
  Reliability Block Diagram (RBD) used for SIL verification
  Event Tree Analysis (ETA) used to confirm frequency of individual hazardous scenarios meet the risk target
Objectives
PFD = Probability of Failure on Demand
PFH = Average frequency of a dangerous failure per hour

## Slide 7
2
Bunker PSS Safety Instrumented Functions

## Slide 8: ID Pattern for Bunker PSS SIFs
System
  Bunker PSS
  Number
1 South-East/North-West Bunker Access Key lock
2 South-East/North-West Bunker LSS Interlock
3 South-East/North-West Bunker Safety Tokens interlock
4 South-East/North-West Bunker Access Door Lock
System_SIFNumber
Notes: There are several SIFs that are expected to be required in each PSS. SIFs 1 to 5 should always be numbered in the same order to facilitate cross-referencing between the systems. Bunker has the additional SIF6 for the Window Guard Interlock.

## Slide 9: Link between SIFs and Risk Assessments
SIF Tag | SIF Name | Hazard ID
BunkerPSS_SIF1_1 | South-East Bunker Access Key (SEB AK) lock | HazID no.6, HazID no.7, HazID no.12
BunkerPSS_SIF1_2 | North-West Bunker Access Key (SEB AK) lock | HazID no.6, HazID no.7, HazID no.12
BunkerPSS_SIF2_1 | South-East Bunker Light Shutters System (LSS) Interlock | HazID no.5, HazID no.6
BunkerPSS_SIF2_2 | North-West Bunker Light Shutters System (LSS) Interlock | HazID no.5, HazID no.6
BunkerPSS_SIF3_1 | South-East Bunker Safety Tokens Interlock | HazID no.1, HazID no.5, HazID no.9
BunkerPSS_SIF3_2 | North-West Bunker Safety Tokens Interlock | HazID no.1, HazID no.5, HazID no.9
BunkerPSS_SIF4_1 | South-East Bunker Access Door Lock | HazID no.3, HazID no.7, HazID no.6
BunkerPSS_SIF4_2 | North-West Bunker Access Door Lock | HazID no.3, HazID no.7, HazID no.6

## Slide 10: Bunker PSS SIFs
BunkerPSS_SIF1_1
If any of the LSS in SEB D01 is detected open, lock the SEB AK in position ON in slot 20 of Unit 1.
Sensors:
  5 Light Shutters in D01 (1oo2 magnetic + mechanical switch)
Logic solver:
  Bunker PSS PLC
  Actuators:
  SEB AK key (solenoid)
Reset conditions:
The SIF shall prevent unlocking the SEB AK from slot 20 of key exchange unit#1 until all light shutters are closed.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 11: Bunker PSS SIFs
BunkerPSS_SIF1_2
If any of the LSS in NWB D03 is detected open, lock the NWB AK in position ON in slot 18 of Unit 1.
Sensors:
  11 Light Shutters in D03 (1oo2 magnetic + mechanical switch)
Logic solver:
  Bunker PSS PLC
  Actuators:
  NWB AK key (solenoid)
Reset conditions:
The SIF shall prevent unlocking the NWB AK from the slot 18 of key exchange unit#1 until all light shutters are closed.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 12: Bunker PSS SIFs
BunkerPSS_SIF2_1
If the South-East Bunker Access key (SEB AK) is detected removed from position ON in Slot 20, de-energise the power contactors for the LSS in D01.
Sensors:
  Bunker South-East access key (Key switch)
Logic solver:
  Bunker PSS PLC
  Actuators:
  5 Light Shutter Systems (LSS) Actuators in D01 (1oo2 contactors)
Reset conditions:
The reset conditions for BunkerPSS_SIF2_1 are the following:
• The BOT MK is in OFF position in Slot 12
• SEB AK is in ON position in slot 20
• All safety tokens are in place
• No inhibit opening the light shutters from Target PSS
• The SEB PSS LSS bypass key is in OFF position.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 13: Bunker PSS SIFs
BunkerPSS_SIF2_2
If the North-West Bunker Access key (NWB AK) is detected removed from position ON in Slot, 18 de-energise the power contactors for the LSS in D03.
Sensors:
  Bunker North-West access key (Key switch)
Logic solver:
  Bunker PSS PLC
  Actuators:
  11 Light Shutter Systems (LSS) Actuators in D03 (1oo2 contactors)
Reset conditions:
The reset conditions for BunkerPSS_SIF2_2 are the following:
• The BOT MK is in OFF position in Slot 12
• NWB AK is in ON position in slot 18
• All safety tokens are in place
• No inhibit opening the light shutters from Target PSS
• The NWB PSS LSS bypass key is in OFF position
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 14: Bunker PSS SIFs
BunkerPSS_SIF3_1
If any safety token is detected removed from unit 3 in South-East Bunker (SEB) PSS, lock the SEB Access Key in unit 2, slot 1 in place by de-energising the solenoid, to
• Prevent initiating proton beam on Target, and
• Prevent opening the Light Shutters System (LSS) in SEB D01.
Sensors:
  Safety circuits from Bunker South-East (1oo2 Solenoid safety circuit)
  Logic solver:
  Bunker PSS PLC
  Actuators:
  Slot 1 of the key exchange Unit 2 of the South-East Bunker (solenoid)
Reset conditions:
The SEB PSS shall prevent unlocking the SEB AK until all safety tokens are returned to key exchange unit3.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 15: Bunker PSS SIFs
BunkerPSS_SIF3_2
If any safety token is detected removed from unit 3 in North-West Bunker (NWB) PSS, lock the NWB Access Key in position ON in unit 2, slot 1 by de-energising the solenoid, to
• Prevent initiating proton beam on Target, and
• Prevent opening the Light Shutters System (LSS) in NWB D03.
Sensors:
  Safety circuits from Bunker North-West (1oo2 Solenoid safety circuit)
  Logic solver:
  Bunker PSS PLC
  Actuators:
  Slot 1 of the key exchange Unit 2 of the North-West Bunker (solenoid)
Reset conditions:
The NWB PSS shall prevent unlocking the NWB AK until all safety tokens are returned to key exchange unit 3.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 16: Bunker PSS SIFs
BunkerPSS_SIF4_1
If the South-East Bunker (D01) Access Key (SEB AK) is removed from Unit 2 slot 1, lock the access door to SEB.
Sensors:
  SEB AK position monitoring (key switch)
  Logic solver:
  Bunker PSS PLC
  Actuators:
  Fortress lock unit on the SEB access door (solenoid)
Reset conditions:
A manual reset shall be required if BunkerPSS_SIF4_1 is tripped:
• by returning the SEB AK to position ON in slot1 of unit2.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 17: Bunker PSS SIFs
BunkerPSS_SIF4_2
If the North-West Bunker (D03) Access Key (NWB AK) is removed from Unit 2 slot 1, lock the access door to NWB.
Sensors:
  NWB AK position monitoring (key switch)
  Logic solver:
  Bunker PSS PLC
  Actuators:
  Fortress lock unit on the NWB access door (solenoid)
Reset conditions:
A manual reset shall be required if BunkerPSS_SIF4_2 is tripped:
• by returning the NWB AK to position ON in slot1 of unit2.
Notes: Jump to RBD for each SIF in the report. Don’t need to read slides

## Slide 18
Safety Requirements Specification (SRS)
3

## Slide 19: Bunker PSS SRS
See ESS-5342379
SIS Logic Solver reqs
  BunkerPSS_SIF1_1 reqs
  BunkerPSS_SIF1_2 reqs
  BunkerPSS_SIF2_1 reqs
  BunkerPSS_SIF2_2 reqs
  BunkerPSS_SIF3_1 reqs
  BunkerPSS_SIF3_2 reqs
  BunkerPSS_SIF4_1 reqs
  BunkerPSS_SIF4_2 reqs
Notes: SRS details of all of the crucial functional and integrity requirements for the logic lover and the SIFs.

## Slide 20
Bunker PSS
SIL Assessment
4

## Slide 21: SIL Assessment Results
Bunker PSS High Demand SIFs
SIS Logic Solver SIL Target | SIL 2 based on the highest SIL target of all SIFs implemented on the Bunker PSS Safety PLC
SIF Tag | Selected PFH Target | PFH Achieved (/hr) | Selected SIL Target | Max Allowable SIL (Architectural Constraints) | Result
BunkerPSS_SIF1_1 – SEB AK Lock | 3.0E-6 | 1.0E-7 | SIL 1 | SIL 2 | Passed
BunkerPSS_SIF1_2 – NWB AK Lock | 3.0E-6 | 1.2E-7 | SIL 1 | SIL 2 | Passed
BunkerPSS_SIF2_1 – SEB LSS Interlock | N/A | 4.3E-8 | SIL 1 | SIL 2 | Passed
BunkerPSS_SIF2_2 – NWB LSS Interlock | N/A | 6.7E-8 | SIL 1 | SIL 2 | Passed
BunkerPSS_SIF3_1 – SEB Safety Tokens Interlock | 3.0E-7 | 1.2E-7 | SIL 2 | SIL 2 | Passed
BunkerPSS_SIF3_2 – NWB Safety Tokens Interlock | 3.0E-7 | 1.2E-7 | SIL 2 | SIL 2 | Passed
BunkerPSS_SIF4_1 South-East Bunker Access Door Lock | 1.7E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
BunkerPSS_SIF4_2 North-West Bunker Access Door Lock | 1.7E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
Notes: SIS Logic Solver SIL Target: SIL 2 based on the highest SIL target of all SIFs implemented on the Bunker PSS Safety Programmable Logic Controller (PLC)

## Slide 22
Bunker PSS
Event Tree Analysis
4

## Slide 23: Event Tree Analysis (ETA)
ETA01a – Access initiated from MCR to the South-East Bunker while LSS is Open (LSS are not failsafe), Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 24: Event Tree Analysis (ETA)
ETA01b – Access initiated from MCR to the North-West Bunker while LSS is Open (LSS are not failsafe), Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 25: Event Tree Analysis (ETA)
ETA2a – BoT operation started in error (while person is in South-East Bunker), Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 26: Event Tree Analysis (ETA)
ETA2b – BoT operation started in error (while person is in North-West Bunker), Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 27: Event Tree Analysis (ETA)
ETA02c - BoT started in error while personnel in the pit (outside bunker), Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 28: Event Tree Analysis (ETA)
ETA03a - Inadvertent opening of the LSS while person is present in the South-East Bunker PSS controlled area, Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 29: Event Tree Analysis (ETA)
ETA03b - Inadvertent opening of the LSS while person is present in the North-West Bunker PSS controlled area, Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 30: Event Tree Analysis (ETA)
ETA04a - Personnel attempt to access Bunker South-East PSS controlled area via Access Door during BoT operation, Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 31: Event Tree Analysis (ETA)
ETA04b - Personnel attempt to access Bunker North West PSS controlled area via Access Door during BoT operation, Radiation hazard
Notes: The failure of search has been credited with a PFD of 0.001 based on search for a small area by trained personnel following written procedure 0.01, supported by Bunker PSS provides another order of magnitude for the PFD (0.1).

## Slide 32: Notes
Recommendations
The following recommendations are proposed for consideration:
• Once operational, track the record for the successful implementation of the procedures and ensure all stakeholders are trained and challenged regularly on the procedure.
• Once operational, gather failure data of SIF elements. Once enough data has been gathered, perform statistical analysis to verify the failure data used in this SIL Assessment.
Notes: No SIFs for ETA01a and ETA02a.

## Slide 33: Thank you for your attention!