## Slide 1: SPL thermal studies
Rossana Bonomi
Rossana.Bonomi@cern.ch
ESS Retreat Meeting, Lund, 28-29/11/2012

## Slide 2: Outline
Short cryomodule heat loads and refrigeration powers
Thermal analyses of components
  Double-walled tube
  Cold-warm transition
  Vacuum vessel and thermal shield
Mock-up test
ESS Retreat Meeting, Lund, 28-29/11/2012
1

## Slide 3: Short Cryomodule
ESS Retreat Meeting, Lund, 28-29/11/2012
2

## Slide 4: Short Cryomodule
RF Power Coupler
Bulk Niobium 5-cells cavity
Helium Tank
CEA’s tuner
Hom Coupler
Bi-phase helium tube
Magnetic shielding
(old design)
Inter-cavity support
Bellows
Double walled tube
ESS Retreat Meeting, Lund, 28-29/11/2012
3

## Slide 5: Cryomodule temperature levels
Heat contributions from:
Double-walled tube to 2 K, 4.5 K
Cold-warm transition to 2 K, 50-70 K
Vacuum vessel to 50-70 K
Thermal shield to 2 K
ESS Retreat Meeting, Lund, 28-29/11/2012
Temperature levels:
Bath 2 K
Inlet helium gas 4.5 K
Thermal shield 50-70 K
Vacuum vessel 300 K
TS
VV
CM
CWT
DWT
4

## Slide 6: Cryomodule heat loads
Subassembly | Type | Source | Desti-nation | @ 2 K [W] |  |  |  | @ 4.5 K [W] |  |  |  | @ 50-70 K [W]
Double-walled tube DWT | cd rad RF | DWT | bath | 13 (1) x 5 = 65 | 0.1 (2) x 5 = 0.5 | 0.5 (3) x 4 + 0.1 x 1 = 2.1 | 22 (4) x 4 + 13 x 1 = 101 | - | - | - | - | -
 | cv | DWT | gas | - | - | - | - | - (1) | 60 (2) x 5 = 300 | 60 (3) x 5 = 300 | - (4) | -
Cold-warm transition * CWT | cd | WF | TS | - |  |  |  | - | - | - | - | 23.0 x 2 = 46.0
 | cd | TS | CM | 0.8 x 2 = 1.6 | 0.8 x 2 = 1.6 | 0.8 x 2 = 1.6 | 0.8 x 2 = 1.6 | - | - | - | - | -
 | rad | WF + wall | CM | 1.0 x 2 = 2.0 | 1.0 x 2 = 2.0 | 1.0 x 2 = 2.0 | 1.0 x 2 = 2.0 | - | - | - | - | -
 | rad | WF | TS | - | - | - | - | - | - | - | - | 0.2 x 2 = 0.4
Vacuum vessel VV | rad ** | VV | TS | - | - | - | - | - | - | - | - | 33.0
Thermal shield TS | rad ** | TS | CM | 1.1 | 1.1 | 1.1 | 1.1 | - | - | - | - | -
Cavity *** | RF | cavity | CM | - (1) | - (2) | 20.0 (3) x 4 = 80.0 | 20.0 (4) x 4 = 80.0 | - | - | - | - | -
TOT for SCM [W] |  |  |  | 69.7 (1) | 5.2 (2) | 86.8 (3) | 185.7 (4) | - | 300 (2) | 300 (3) | - | 79.4
DWT Static heat loads
(1) RF off, cool off
(2) RF off, cool on
DWT Dynamic heat loads
(3) RF on, cool on
(4) RF on, cool off
* Thermal shield at 50 K, placed at 0.15 m from cold flange
** C. Maglioni, V. Parma’s technical note: “Assessment of static heat loads in the LHC arc, from the commissioning of sector 7-8”, LHC Project Note 409, 2008 (VV TS 1.7 W/m2 - TS  CM 0.1 W/m2)
*** V. Parma’s presentation: http://cdsweb.cern.ch/record/1302738/files/thp004.pdf
5

## Slide 7: Cryomodule refrigerator powers
@ 2 K (990 Wel/Wth*):
@ 50-70 K (16 Wel/Wth*):
@ 4.5 K - DWT cooling:
  40 mg/s warm gas are equivalent to 4 Wth @ 4.5 K (100 Wth/(g/s))
  4 Wth @ 4.5 K cost 880 Wel (220 Wel/Wth*)
  For 4+1 DWT  4.4 kWel
(1) | 70 Wth | 69.3 kWel
(2) | 5 Wth | 5.0 kWel
(3) | 87 Wth | 86.1 kWel
(4) | 186 Wth | 184.1 kWel
Static operations
Dynamic operations
 | 79 Wth | 1.3 kWel
* S. Claudet et al. “1.8 K Refrigeration Units for the LHC: Performance Assessment of Pre-series Units”, proceedings ICEC20
(@ 2 K: 15% Carnot, @ 50-70 K: 30% Carnot, @ 4.5 K: 30% Carnot)
6

## Slide 8: Cryomodule refrigerator tot power
Around 92 kWel of refrigerator power are expected during nominal operation for the SPL short cryomodule (4 cavities)
Heat loads due to instrumentation and critical regions are disregarded
ESS Retreat Meeting, Lund, 28-29/11/2012
7

## Slide 9: Double-walled tube
Semi-analytical model*
1D, 3 layers, 22 nodes
L = 300 mm
D = 50 mm
S = 1152 mm2
m = 40 mg/s
* Based on O. Capatina ‘s presentation: http://indico.cern.ch/getFile.py/access?contribId=3&resId=1&materialId=slides&confId=86123
8

## Slide 10: Double-walled tube
Results are comparable with FE 2D simulations (Comsol)
  Heat load at bath:
  < 0.5 W
  RF power: 10.1 W
  Antenna radiation load: 0.6 W
ESS Retreat Meeting, Lund, 28-29/11/2012
9
No COOL
40 mg/s He

## Slide 11: Double-walled tube
RF currents node position is critical ..
ESS Retreat Meeting, Lund, 28-29/11/2012
Shift [mm] | Prf [W] | Qrad (W) | Qbath [W]
0 | 10.189 | 0.579 | 0.110
50 | 15.503 | 0.581 | 0.375
100 | 14.077 | 0.587 | 0.576
150 | 8.213 | 0.586 | 0.346
200 | 8.802 | 0.580 | 0.113
250 | 14.512 | 0.580 | 0.278
300 | 15.252 | 0.586 | 0.571
RF currents
10

## Slide 12: Thermodynamic efficiency of DWT gas cooling
(Figure from: « An Introduction to Cryogenics », Ph.Lebrun, CERN/AT 2007-1)
He refrigeration He Liquefaction
Electrical power for liquefaction of 1 g/s helium: 6200 Wel
Carnot COP @ 4.5 K: 66 Wel/Wth
1 g/s liquid helium is equivalent to 100 Wth @ 4.5 K *
11
* U. Wagner s presentation: http://cdsweb.cern.ch/record/808372/files/p295.pdf

## Slide 13: Thermodynamic efficiency of DWT gas cooling
Comparison with other ways of cooling (heat intercepts, self-sustained cooling)
990 @ 2 K, 220 @ 9 or 4.5 K, 16 @ 80 K
ESS Retreat Meeting, Lund, 28-29/11/2012
Case | Q @ 2K [W] | P [Wel] | Q @ 9K [W] | P [Wel] | Q @ 80K [W] | P [Wel] | vapours rate [g/s] | Q equiv. @ 4.5K [W] (1g/s=100W) | P [Wel] | Total power [Wel]
A) No intercept | 12.6 | 12,375 | - | - |  |  | - | - | - | 12,375
B) 1 optimised intercept @ 80K | 2.2 | 2,178 | - | - | 44.6 | 714 | - | - | - | 2,892
C) 2 optimised intercepts @ 80K & 9K | 0.18 | 178 | 3.2 | 704 | 30.6 | 490 | - | - | - | 1,372
D) 4.5K self-sustained vapour cooling | 0.03 | 30 | - | - | - | - | 0.020 | 2 | 440 | 470
E) He vapour cooling (4.5K-300K) | 0.10 | 99 | - | - | - | - | 0.04 | 4 | 880 | 979
F) He vapour cooling (4.5K-300K), RF power on | 0.50 | 495 | - | - | - | - | 0.04 | 4 | 880 | 1,375
G) No He vapour cooling, RF power on | 22 | 21,780 | - | - | - | - | 0 | 0 | 0 | 21,780
12

## Slide 14: Cold-warm transition
Mathcad/Matlab analytical analysis for each position and temperature of thermal shield
Heat due to radiation and to conduction are evaluated
ESS Retreat Meeting, Lund, 28-29/11/2012
TS
13
Equivalent electric

## Slide 15: Cold-warm transition
ESS Retreat Meeting, Lund, 28-29/11/2012
Heat to TS [W]
Heat to BATH [W]
Cold flange
Warm flange
IDEAL refr power [kWel]
Cold flange
Warm flange
14

## Slide 16: Vacuum vessel and thermal shield
Radiation values rescaled from LHC commissioning of sector 7-8
LHC linear heat loads (average values):
  4.3 W/m vacuum vessel to thermal shield
  0.2 W/m thermal shield to cold mass
For SPL SCM:
  33.0 W @ TS from vacuum vessel
  1.1 W @ 2 K from thermal shield
* C. Maglioni, LHC Project Note 409 - http://cdsweb.cern.ch/record/1087253/files/project-note-409.pdf
15

## Slide 17: Mock-up test
ESS Retreat Meeting, Lund, 28-29/11/2012
1.5 cavities
2 DWTs
1 intercavity support
Cooled by LN2 (rescaling to He)
Test of all possible cooling conditions
No RF power
16
Validation of:
  Cavity supporting system
  Assembly-realignment of cavities via vessel interface
  Alignement measurign device (OWPM)
  Thermal contractions
  DWT active cooling

## Slide 18: Mock-up test
ESS Retreat Meeting, Lund, 28-29/11/2012
17

## Slide 19: Questions?
Cliffside Gas Field, Amarillo – TX (2012)
..save Helium (for pacific purposes)!
The National Helium Reserve, also known as the Federal Helium Reserve, is a strategic reserve of the United States holding over a billion cubic meters (1E9 m3) of helium gas.
The helium is stored at the Cliffside Storage Facility about 12 miles northwest of Amarillo, Texas, in a natural geologic gas storage formation, the Bush Dome reservoir.
The reserve was established in 1925 as a strategic supply of gas for airships, and in the 1950s became an important source of coolant during the Space Race and Cold War.
The natural gas in these fields contains unusually high percentages of helium, from 0.3% to 2.7%; they constitute the largest source of helium in the United States. The helium is separated as a byproduct from the produced natural gas.
After the Helium Acts Amendments of 1960, the U.S. Bureau of Mines arranged for five private plants to recover helium from natural gas. For this helium conservation program, the Bureau built a 425-mile pipeline from Bushton, Kansas, to connect those plants with the government's partially depleted Cliffside gas field. This helium-nitrogen mixture was injected and stored in the Cliffside gas field until needed, when it then was further purified.
(source: Wikipedia)
18

## Slide 20
Thanks for your attention! Tack för din uppmärksamhet !
Participants to the collaboration effort:
System/Component/Activity | Person(s) in charge | Lab
Cavities/He vessel/tuner construction | O.Brunner, O.Capatina, Th.Renaglia, F.Pillon, N.Valverde, M.Esposito, I.Aviles, G.Devanz | CERN CEA-Saclay
SRF, magnetic shielding, Clean-Room activities, RF test stations (SM18) | E.Ciapala, T.Junginger, K.Shirm, J.Chambrillon, O.Brunner | CERN
RF Coupler | E.Montesinos, G.Devanz | CERN CEA Saclay
Vacuum systems | G.Vandoni | CERN
Cryogenics (cryo infrastructure SM18) | O.Pirotte | CERN
Survey and alignment | P.Bestman | CERN
Cryo-module conceptual design | R.Bonomi, O.Capatina, P.Coelho, V.Parma,T.Renaglia, A.Vande Craen, L.R.Williams | CERN
Cryo-module detailed design & Integration & Cryostat assembly tooling | P.Dambre, P.Duthil, P.Duchesne, S.Rousselot, D.Reynet | CNRS/IPNO-Orsay
SPL Machine architecture | F.Gerigk | CERN
ESS Cryomodule developments | C.Darve | ESS
Cryo-module Technical Coordination | V.Parma | CERN

## Slide 22: Master schedule
ESS Retreat Meeting, Lund, 28-29/11/2012

## Slide 23: SPL operational conditions
ESS Retreat Meeting, Lund, 28-29/11/2012

## Slide 24: SPL operational conditions
ESS Retreat Meeting, Lund, 28-29/11/2012
Operating condition | Value | 
Beam current/pulse lenght | 40 mA/0.4 ms beam pulse | 20 mA/0.8 ms beam pulse
cryo duty cycle | 4.11% | 8.22%
quality factor | 10 x 109 | 5 x 109
accelerating field | 25 MV/m | 25 MV/m
Source of Heat Load | Heat Load @ 2K | 
Beam current/pulse lenght | 40 mA/0.4 ms beam pulse | 20 mA/0.8 ms beam pulse
dynamic heat load per cavity | 5.1 W | 20.4 W
static losses | <1 W (tbc) | <1 W (tbc)
power coupler loss at 2 K | <0.2 W | <0.2 W
HOM loss in cavity at 2 K | <1 | <3 W
HOM coupler loss at 2 K (per coupl.) | <0.2 W | <0.2 W
beam loss | 1 W | 
Total @ 2 K | 8.5 W | 25.8 W

## Slide 25: Ideal vs. real refrigerator power
Temperature level [K] | IDEAL - Carnot [Wel/Wth] | REAL [Wel/Wth] | Efficiency wrt Carnot [%]
2 | 149 | 990 | 15
4.5-9 | 66-32 | 220 | <30
50-70 | 5-3 | 16 | <30
ESS Retreat Meeting, Lund, 28-29/11/2012

## Slide 26: (B) 1 Heat intercept
ESS Retreat Meeting, Lund, 28-29/11/2012
Q @ 2K
300K
x1
L
Q @ 80K

## Slide 27: (C) 2 Heat intercepts
ESS Retreat Meeting, Lund, 28-29/11/2012
Q @ 2K
300K
Q @ 8K
Q @ 80K
L
x1
x2

## Slide 28: (D) He vapour cooling
300K
4.5K
Q in g/s
L
ESS Retreat Meeting, Lund, 28-29/11/2012
attenuation factor

## Slide 29: LHC Multi layer insulation (MLI)
ESS Retreat Meeting, Lund, 28-29/11/2012
Features:
1 blanket (10 reflective layers) on cold masses (1.9 K)
2 blankets (15 reflective layers each) on Thermal Shields (50-65 K)
Reflective layer: double aluminized polyester film
Spacer: polyester net
Stitched Velcro™ fasteners for rapid mounting and quality closing
Interleaved reflectors and spacers
1 blanket on CM, 2 on thermal shield
Velcro™ fasteners
Blanket manufacturing

## Slide 30: SCM instrumentation