## Slide 1: Overview over CEA Saclay RF test stands and use of the FMC IOxOS ADC3111 board
Alexis Gaget & Françoise Gougnaud
with Daniel Bogard, Adelino Gomes
CEA Saclay Irfu
EPICS meeting May 2016

## Slide 2: OUTLINE
CEA control packages in the ESS collaboration
ESS control box for RF test stands
The 704 MHz pulsed RF source test stand
Control of the RF source for the coupler conditioning test
Requirements for conditioning fast acquisition
Solutions selected by ESS ICS
Measurement of the ESS ICS driver
Results according to our context
Modifications
Measurement including our modifications

## Slide 3: CEA control packages in the Collaboration
  Source and LEBT control at Catania
  Contribution for the RFQ control
  Several RF test stands at Saclay for ESS
  Cavity coupler conditioning test with the currently RF 704 MHz source
  RF power tests on the ESS prototype cryomodule ECCTD
  ESS RFQ coupler conditioning test with the pulsed RF 352 MHz source NEW and late 2016
  704 MHz pulsed RF source to test the power couplers for ESS linac NEW and summer 2017

## Slide 4: Ess control box for RF test stands
  Choice to use EPICS for Saclay RF test stands
  Fast acquisition needed by the different coupler conditioning tests
  Choice to use the VME64X ESS platform (first one available) based on IOxOS boards for Saclay RF test stands with the ESS EPICS Environment
  See “ESS EPICS Environment Integration at CEA Saclay” by Nicolas Senaud
Beckhoff on EtherCAT
MRF Timing System
IOxOS CPU 1210
with FMC ADC3111

## Slide 5: the 704 MHz pulsed RF source test stand
  The 704 MHz pulsed RF source will be used for the prototype and series coupler conditioning test
  Heterogeneous controls of HV modulator and klystron are being moved to EPICS

## Slide 6: Control of the RF source AND the coupler conditioning TEST STAND
Interlocks
PLC V350 Unitronix
Beckhoff/EtherCAT
NISE 3500 IPC
Channel Access
Modbus/Tcp
HV Modulator
Klystron 704MHz
LAN
ESS VME/IOxOS
GPIB
Water
vacuum
Safety
RF
Security box
Archiver
Appliance
CEA EEE

## Slide 7: Requirements for conditioning fast acquisition
Hardware Requirements
  Sampling rate from 250KSamples/s up to 1MSamples/s
  External trigger to synchronize the acquisitions
  At least 18 channels
Software requirements
  Display windows from 5ms up to 10ms at 1MS/s -> Waveform up to 10000 samples
  Sampling rate configurable
  Measurement functions (min, max, average, sum ...) using configurable cursor and threshold
  Non linear conversion

## Slide 8: Solution selected by ess ics
  Ioxos ifc1210 single board adc3111 fast acquisition mezzanine card
  8 channels
  External trigger
  16 bits resolution
  Sampling rate : 50KSamples/s up to 250MSamples/s
  Up to 16384 Samples per channel
  +/- 0.5V Range
  DC Coupling
  VME64x
  Realtime Linux
  CPU 1.2GHz
  1 slot FMC
  1 slot FMC / PMC
  2 Ethernet slots
PSI EPICS Driver updated by ESS ICS
  Waveform up to 16384
  Sampling rate configurable
  Configurable trigger (source, delay, edge …)
  Measurement function (min, max, top average...etc)
  Oscilloscope type function (gain, offset...etc)
  Linear conversion
  Common interface for a family of ADC modules (ADC3310, ADC3111, D-tAcq …)

## Slide 9: Measurement of the ess ics driver
Chart: 
| 16 | 5000 | 10000 | 15000 | 16384
250ks/s | 3 | 11 | 12 | 16 | 17
greater 1MS/s | 3 | 12 | 21 | 30 | 33
Conditions
  ESS ICS EPICS Database
  14Hz repetition frequency
  16 channels
  Pulses from 16 samples to 16384 samples
  Sampling rate from 250KS/s to 1MS/s
  Memory : 51,2%
  Network : 14Mo
  Load average: up to 30%
ifc1210 single board results
CPU
Samples

## Slide 10
  All PVs provided are not necessary
  Linear conversion is useful but also non linear conversion needed
  Too much network used, no need to display so many samples
  Available measurement functions not useful (no cursor)
Results according to our context

## Slide 11
  Development of an EPICS module « FastAcquisition » using only needed record
  Development of an EPICS module « DataProcessing » to measure each channel with its owns cursors, returns a compressed waveform of N samples (configurable) and converts a waveform using a non linear function
| PAGE 11
FastAcquisition
DataProcessing
(conversion, cursor, average signal…)
EPICS Events
Signal waveform
EPICS PSI Driver
Updated by ICS
Signal
EPICS
EPICS
Modifications

## Slide 12: Measurement including our modifications
Conditions
  With non linear conversion and processing
  14Hz repetition frequency
  16 channels
  Pulses from 5000 samples to 16384 samples
  Sampling rate from 250KS/s to 1MS/s.
  Memory : 5%
  Network : 1Mo
  Load average: up to 100%
  Some reboot and freeze
Chart: 
| 5000 | 10000 | 12000 | 13000 | 14000 | 15000 | 16384
250KS/s | 0.43 | 0.38 | 0.44 | 0.46 | 0.48 | 0.5 | 0.53
greater 1MS/s | 0.43 | 0.73 | 0.84 | 0.87 | 0.88 | 0.9 | 0.93
  Our need is respected : 10000samples at 1MS/s
CPU
Samples
ifc1210 single board results

## Slide 13
| PAGE 13
conclusion
We are ready for the coupler
conditioning test
Many thanks to ESS ICS
support and efficiency