## Slide 1: ASYN based S7 PLC Driver
Jignesh Patel
Ralph Lange, Bruno Evrard, Prasad Sawantdesai*
ITER Organization
Control System Division
*Tata Consultancy Services

## Slide 2: Contents
  Slow Controller development
    Slow Controllers : S7 PLCs
    Data flow – System Perspective
  s7PLCAsyn Driver
    Status and Features
    Communication Model
    CODAC Frame
    Redundant PLCs
    Event Interface
  Standard PLC Software Structure (SPSS)
  Development and Integration
    PLC Application Development Workflow
    SDD Generated Software Unit
    Deployment
  Plan

## Slide 3
ITER’s Slow Controller: S7
Hardware catalogue defines S7 for Slow Controller
S7-400 & S7-300, Fail Safe (F), High availability(H)
CODAC Core System uses the PSI S7PLC + ITER Extension support and the newly developed s7PLCAsyn support

## Slide 4
Data Flow

## Slide 5
s7PLCAsyn status
Latest release will be v1.3 with CODAC Core System v5.3, in distribution from CCSv5.0
Support existing driver functionality i.e. Block transfer with ITER Extensions, new features
  Single PLC
  Redundant PLCs
Different communication channels state & configuration, simple command, event
CODAC Frame in block transfer – to support system health monitoring and smooth integration

## Slide 6
s7PLCAsyn status
Native S7 protocol support using nodave (Block, single variable)(cont...)
ISO-on-TCP support using interpose layer (cont...)
……
……

## Slide 7
s7PLCAsyn Features
Modular design due to ASYN
Generic ASYN device support on top of drvAsynIPPortDriver
Swappable Low level protocol drivers without changing EPICS database
i.e. INP and OUT links are independent from the protocol being used
Scalable for new features and protocols

## Slide 8
Communication Model

## Slide 9
Communication Model

## Slide 10
States (from PLC)
  as fast as possible
  50ms for Redundant PLCs
  State CODAC Frame
Configuration (to PLC)
  Every 100ms, on change
  Configuration Control on start of IOC to avoid reset of PLC using auto save functionality
Simple Commands (to PLC)
  Every 100ms, on change
  Sets a Boolean variable to “TRUE”, using “HIGH” field for reset.
  Push-button like functionality
Event (from PLC)
  Time-stamped bool events, on change
  Captures all changes in PLC with PLC cycle resolution
  Event CODAC Frame
Communication Model – PLC to PLC IOC Interface

## Slide 11
Port driver uses two TCP connections to Redundant PLCs using IPPort driver
i.e. state/configuration channel and Simple Command channel
Records get processed from PLC states with latest time stamps, old timestamp ignored.
Online Redundancy management using the redundancy status bits sent from PLC
Configuration and Simple commands always sent to both PLCs if live and active
Redundant PLCs

## Slide 12
Its similar to state interface with some special characteristics.
Interface to capture time stamped Boolean events with order of occurrence.
Time stamped with PLC cycle resolution.
Useful for post diagnostics in case of chain of actions happening fast.
Virtually there is no traffic in absence of Events
Heart beat packet sent by PLC to maintain connection status, but does not trigger record processing.
Event Interface

## Slide 13
Part of State and Event channel block transfer
Supported by SPSS (Standard PLC Software Structure), nothing but standard PLC Application
  PLC Timestamps
  Communication Block length
  Alive counter (states), Frame counter (event), Heartbeat (event)
  Application version to ensure consistency between PLC and IOC (states)
  Redundancy status i.e. Master, Slave, Active, Valid (states)
  Header, Footer
  NTP status bit (event) (partial)
CODAC Frame

## Slide 14
SPSS
  PLC Software package, deployed on all PLCs
  Implements common architecture for the PLC Software
  structured communication mechanism between the PLC and the PSH
  Implements communication Interface with CODAC
    PLC Interface – OpenIE (TSEND, TRECV)
    CP Interface – send/receive (AG_SEND, AG_SECV, AG_LSEND, AG_LRECV)
  SPSS Packages are part of CCS release
    PLC_Interface
    CP_Interface
    PLCCP_Interface
    Redundant_PLC (CP Interface)
  Standard PLC Software Structure (SPSS)

## Slide 15
  Standard PLC Software Structure (SPSS)

## Slide 16
  PLC Application Development Workflow
SDD – Self Description Data toolkit

## Slide 17
  SDD Generated Software Unit
EPICS Records
EPICS PLC IOC
Alarms Configuration
Archives Configuration
Generated HMI
PLC Interface files
awl - interface data blocks
sdf - symbol definitions
xlsx - variable table

## Slide 18
  Deployment
Mini-CODAC
Mini-CODAC
PSH
PSH IOC
PLC IOC
PLC
Communication
OPIs
Alarm
Server
Archive
Engine
Processing
I/O
Local SDD
SDD Editor
SDD Translator:
m-<I&C_Project_Name>/
Local
File System
SPSS
(S7 Program Standard Template)
/opt/codac/step7/STEP7/<SPSS>.zip
CODAC Interface Files
(AWL and SDF)
src/main/plc/
PLC IOC
(EPICS DB and IOC)
src/main/epics

## Slide 19
  Improve redundant driver - lagging tight control/coupling over two IP Port connection made to two redundant PLCs
  Complete full featured implementation of S7 protocol support
  Solution to overcome 32K data block limit of send/recv communication
  To make available pure ASYN S7 driver (independent to CODAC)
  ….
  Plan