## Slide 1: Auxiliary lines – Design overview
Przemysław Jaszak
Jarosław Poliński
Janusz Skrzypacz
Maciej Chorowski
Critical Design Review Meeting, 10-11 January 2017, Wroclaw, Poland

## Slide 2: Auxillary lines – general wiew

## Slide 3: Aux. Lines without external frames
Section I –suport type A
Section II –suport type B
Section III –suport type C

## Slide 4: External supports

## Slide 5: Supports scheme
Sliding supports
Fixed support

## Slide 6: Fixed and sliding support - design

## Slide 7: Special design of the supports
External support in the bunker

## Slide 8: Special design of the supports
External support in vicinity of the warm pipes

## Slide 9: He line and its Vacuum shield

## Slide 10: He line’s supports

## Slide 11: He line’s supports
Sliding supports
Bellow
Fixed support

## Slide 12: He line’s supports
Connection between fixed support and vacuum shield

## Slide 13: Interconnection points
Connection to valve box

## Slide 14: Interconnection points

## Slide 15: External frames - fixation

## Slide 16: External frames - fixation

## Slide 17: External frames - fixation
Fv,Ed =1,36kN– actual value of the shear force
Ft,Ed =4,72kN– actual value of the tensile force

## Slide 18: External frames - fixation
Calculating permisible forces for olt M10 class 8.8 (in accordance to EN 1993-1-8 Eurocode 3
=33,5 kN >
=21,1 kN >
=0,208
Fv,Ed =1,36kN
Ft,Ed =4,72kN

## Slide 19: Corrections

## Slide 20: Corrections
The size of the HP line flange in the interface to TICP should be DN15 instead of DN25

## Slide 21: Clarifications
CV71 and PT71 were missing in the 3D model (see Figure 10). The control valve connects the HP line with the SV relief line (refer to Figure 1 in ESS09915216R1.2)

## Slide 22: Clarifications
There was a lack of a pumping port onto the purge return line at the test stand bunker

## Slide 23
Thank you for attention