| European Spallation Source Cryogenic Distribution System for the Lund Test Stand2 Cold process lines and auxiliary lines sizing |
| --- |
| Type of document | Technical document |
| ESS Contact Person | Jaroslaw FYDRYCH |
| WrUT references | S/263/15-105 |
| Version | 1.1 |
| Publication date | 2017.01.04 |

| Written by | Checked by | Approved by |
| --- | --- | --- |
| Jaroslaw POLINSKI | Jaroslaw POLINSKI |  |
| Signature: | Signature: | Signature: |

Revisions list

| Rev. No | Revision date | Revision scope |
| --- | --- | --- |
| 1.0 | 2016.12.30 | Original document |
| 1.1 | 2017.01.04 | Version with answers to ESS comments to CDR charge |

Content

1.	Introduction	4

2.	Aim of the report	6

3.	Calculation teoretical background	6

4.	Calculations	8

4.1.	Cold main lines	8

4.2.	Cold branch lines	9

4.2.1.	VLP branch line	9

4.2.2.	He Supply branch line	10

4.2.3.	TS Supply branch line	10

4.2.4.	TS Return branch line	10

4.3.	Total pressure drop in the main and branch cold process lines	11

4.4.	Auxiliary lines	11

5.	Summary	12

6.	Reference	12

# Introduction

The CDS for Lund Test Stand 2 is dedicated to transferring cooling power from the TICP to the ESS elliptical cryomodules under their site acceptance tests in the test stand bunker. The system includes a cryogenic transfer line (CTL), one valve box and four auxiliary process lines.

The CTL runs from the TICP cold box in the cold box building to the test stand bunker placed in the klystron gallery. The line is a vacuum insulated multichannel line and its vacuum jacket houses four cold process lines, thermal shield, supports and thermal compensation system. The cryoline ends in the test stand valve box, in which four branch process lines connect the headers with the cryomodule cold circuits. Thus the whole system consists of four main and four branch cold process lines. Their names and acronyms are as follows:

•	helium supply lines: helium supply main line (MC) and helium supply branch line (BC),

•	vapour low-pressure lines: VLP main line (MB) and VLP branch line (BB),

•	thermal shield supply lines: TS supply main line (ME) and TS supply branch line (BE),

•	thermal shield return lines: TS return main line (MF) and TS return branch line (BF).

The process and instrumentation diagram of the CDS is shown in Figure 1.1.

Figure 1.1. Process and instrumentation diagram of the CDS for Lund Test Stand 2

The dimensions and operating conditions of the main and the branch cold process lines are presented in Table 1.1.

Table 1.1.  Design parameters of the main and the branch cold process lines

| Type of process line | Process line name | Process line acronym | Size | Design pressure a | Nominal operating pressure a | Nominal operating temperature |
| --- | --- | --- | --- | --- | --- | --- |
| Main cold process lines (headers) | He supply line | MC | DN15 | 16 bar | 3 bar | 4.5 K |
|  | VLP line | MB | DN65 | 12 bar | 27 mbar | 3 K - 5 K |
|  | TS supply line | ME | DN15 | 22 bar | 12.8 bar | 40 K |
|  | TS return line | MF | DN15 | 22 bar | 12.5 bar | 50 K |
| Branch cold process lines | He supply branch line | BC | DN10 | 16 bar | 3 bar | 4.5 K |
|  | VLP branch line | BB | DN50 | 12 bar | 27 mbar | 3 K - 5 K |
|  | TS supply branch line | BE | DN10 | 22 bar | 12.8 bar | 40 K |
|  | TS return branch line | BF | DN10 | 22 bar | 12.5 bar | 50 K |

a - all pressure values are given as absolute pressures

The CDS-LTS2 includes also 4 auxiliary process lines that connect the tested cryomodule and valve box with the warm compressor station (WCS) of the TICP. The main auxiliary process lines run from the compressor building along the CTL duct and gallery and further to the cold box building and klystron gallery alongside the cryogenic transfer line. There are four main and four branch auxiliary process lines. Their names and acronyms are as follows:

•	high pressure line: HP main line (MH) and HP branch line (BH),

•	purge return line: Purge return main line (MP) and Purge return branch line (BP),

•	safety valve relief line: SV relief main line (MS) and  SV relief branch line (BS),

•	helium recovery line: helium recovery main line (MR) and helium recovery branch line (BR).

The dimensions and operating conditions of the main auxiliary process lines are presented in Table 1.2.

Table 1.2. Design parameters of main auxiliary process lines

| Type of process line | Process line Name | Process line code | Size | Design pressure a | Nominal operating pressure a | Nominal operating temperature |
| --- | --- | --- | --- | --- | --- | --- |
| Main auxiliary process lines (headers) | SV relief line | MS | DN100 b | 6 bar | 1.1 bar | 4K - 300 K |
|  | HP line | MH | DN25 | 16 bar | 3.0 bar | 300 K |
|  | Purge return line | MP | DN50 | 6 bar | 0 bar - - 1.1 bar | 300 K |
|  | Helium recovery line | MR | DN50 c | 6 bar | 1.1 bar | 4 K - 300 K |

a - all pressure values are given as absolute pressures
b - the SV relief line is equipped with a drip tray in the test stand bunker
c - the helium recovery line is vacuum insulated in the klystron gallery and cold box room;
the size of its external envelope is DN100

# Aim of the report

The aim of the report is to confirm the proposed size of the process and auxiliary lines in view of the flow pressure drop specified in Table 12 of [1] and recalled here in Table 2.1.

Table 2.1.  Maximum allowable pressure drops in the cold process and auxiliary lines of the CDS-LTS2

| Process line | Maximum allowable pressure drop | Flow rate in main lines | Calculation pressure a | Calculation temperature |
| --- | --- | --- | --- | --- |
| He supply line | 5 mbar | 3.0 g/s | 3.0 bar | 4.5 K |
| VLP line | 1.5 mbar | 3.0 g/s | 31.3 mbar | 5.0 K |
| TS supply line | 25 mbar | 4.5 g/s | 12.8 bar | 35 K |
| TS return line | 35 mbar | 4.5 g/s | 12.5 bar | 55 K |
| SV relief line | 50 mbar | 50 g/s | 1.05 bar | 300 K |
| HP line | 300 mbar | 6 g/s | 3.0 bar | 300 K |
| Purge return line | 50 mbar | 5 g/s | 1.05 bar | 300 K |
| Helium recovery line | 35 mbar | 6 g/s | 1.05 bar | 300 K |

The values in Table 2.1 for the cold lines are applicable for the ensemble of both the main lines and the branch lines in the valve box and jumper connection.

# Calculation teoretical background

Each line is composed of different pipe pieces as linear pieces, elbow pieces, T-connections or corrugated elements (bellows, elastic hoses) . The fluid flow pressure drop p in the particular piece can be calculated from the following equation:

(3.1)

where:

 - local pressure drop coefficient of the piece - dimensionless

W - fluid mass stream - kg/s

d - internal diameter of the piece through which the fluid flows, m

 - fluid density, kg/m3

In case of fluid flow through the linear piece the local pressure drop coefficient can be calculated from:

(3.2)

where:

- linear pressure drop coefficient - dimensionless

Lp - pipe piece length, m

In the further analysis the  values are calculated from the equation (7.32) [2]:

(3.3)

where:

k - the pipe roughness, m

Re - Reynolds number - dimensionless

In the further calculations the pipe roughness is assumed as 70m, while the Reynolds number is calculated from the following equation:

(3.4)

where:

v - is the fluid velocity, m/s

 - dynamic viscosity of the fluid, Pa.s

The fluid velocity in the circular pipe can be calculated from:

(3.5)

In case of the gas flow through the corrugated elements the linear pressure drop coefficient is increased by factor 1.5 [3].

For the pipe elbows with radius-to-diameter ratio R/d=1.25 the pressure drop coefficient elb=0.203 is taken as per [2] Table 10.6.3 pos. 1.

For the T-connectors with flow inlet from branch side the TB=o=0.91 is taken as per [2] Table 10.6.3 pos. 14 for qV0/qV=1.0.

For T-connectors without outflow to the branch (straight flow) the TS=p=0.04 is taken as per [2] Table 10.6.3 pos. 14 for qV0/qV=0.

In case of the branch line connection with the main line for VPL and TS Return lines the local pressure drop coefficient T =1.0 is accounted as per [2] Table 10.6.3 pos. 33 for the free outlet from the line, what can be  justified by the large branch and main lines diameter difference. For the He Supply and for the TS Supply lines this connection is considered as the inlet to the line and the T =0.5 as per [2] Table 10.6.3 pos. 29.

For the pipe extensions and reductions the local pressure drop coefficient EX or RE is taken from Table 10 pos. 27 and 28 respectively for given D/d ration and extension/reduction angle .

In case of the valves installed in the cold branch lines the pressure drop is calculated with respect of the thermodynamic parameters specified in Table 2.1 and minimum required valve flow coefficient, determined in [4].

For the gas flow through valve the pressure drop is calculated by rearmament of the equation (3.2) [4] to equation (3.5) with assumption that the expansion factor Y≈1 - compare the Y value in [4], Table 4.1:

(3.5)

where:

N6 - constant depend on the unit,  N6= 31.6 for W[kg/h], p [bar a],  [kg/m3],

pin - fluid pressure at the valve inlet, bar a,

in - fluid density at the valve inlet, kg/m3,

while for the liquid flow the pressure drop is calculated by rearmament of the equation (3.7) [4] to equation (3.6)

(3.6)

where:

Q - Volumetric flow rate, m3/h

N1 - constant depend on the unit, N1= 1 for Q[m3/h], p [bar a]

0 - reference density, 0 =1000 kg/m3

# Calculations

## Cold main lines

All main cold process lines are composed of this same line pieced but with different diameter. Only VLP main line has the DN65/D40 reduction (D/d=1.4, =20o, RE=1.3) close to the connection to the TICP. Table 4.1 presents exemplary detail calculation results for VLP main line while Table 4.2 summarises the flow pressure drop calculation assumptions and results for all main lines. In the Table 4.2 values of the fluid density and dynamic viscosity are calculated with [5] for temperature and pressure specified in Table 2.1.

Table 4.1 Calculation results of the pressure drop in the VLP main line

| Piece type | W | L | D | Length/ pcs | Density | Viscosity | Velocity | Re |  |  | Sum  | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | g/s | m | m | m | kg/m3 | 10-6 Pa.s | m/s |  |  |  |  | mbar |
| DN 65 | 3.0 | 56 | 0.069 | 56 | 0.307 | 1.254 | 0.802 | 44143 | 0.0247 | NA | 20.1 | 0.2105 |
| Elbows | 3.0 | NA | 0.069 | 9 | 0.307 | 1.254 | 0.802 | 44143 | NA | 0.23 | 2.07 | 0.0217 |
| DN 40 | 3.0 | 0.5 | 0.0443 | 0.5 | 0.307 | 1.254 | 1.950 | 68817 | 0.0247 | 0.266 | 0.267 | 0.0165 |
| Reduction DN65/DN40 | 3.0 | NA | 0.0443 | 1 | 0.307 | 1.254 | 1.950 | 68817 | 0.0247 | 1.3 | 1.3 | 0.0805 |
| Total | 0.3292 |

Table. 4.2 Summary of the flow pressure drop calculation assumptions and results for 
He Supply, TS Supply and TS Return lines

| Line name | Nominal diameter | Linear piec. total length | Reduced diameter | Reduced diameter length | Elbow pcs. | Mass flow | Density | Velocity | Viscosity | Total press. drop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | - | m | - | m | - | g/s | kg/m3 | m/s | 10-6 Pa.s | mbar |
| VLP | DN65 | 55.5 | DN40 | 0.5 | 9 | 3.0 | 0.307 | 0.80 | 1.254 | 0.329 |
| He Supply | DN15 | 56 | NA | NA | 9 | 3.0 | 129.7 | 12.8 | 3.472 | 0.621 |
| TS Supply | DN15 | 56 | NA | NA | 9 | 4.5 | 17.23 | 1.11 | 5.39 | 10.53 |
| TS Return | DN15 | 56 | NA | NA | 9 | 4.5 | 10.76 | 1.78 | 6.95 | 17.11 |

## Cold branch lines

VLP branch line

For T=5K and p=31.3 mbar the density of helium is determined with [5] and =0.307 kg/m3 while its dynamic viscosity is =1.254 Pa.s. Mass flow in the VLP branch line is 3.0 g/s.

The valve box branch VLP line is composed of:

- total 3.9 m of linear DN50 pieces

- 1 × DN50, 0.31m long elastic hose. The influence of the hose on the pressure drop is included in the calculations by increasing the total length of the branch line linear pieces by 0.31x1.5=0.47m

- 6 × DN50 elbow

- 1 × DN50 T-connection (straight flow - TS=0.04)

- 1 x DN50 valve (CV04) - pressure drop is calculated from (3.5):

- 1 x free outlet from the line

The calculated pressure drop in the VLP branch line is presented in the Table 4.2

Table. 4.2. Calculation results of the flow pressure drop in the branch VLP line

| Piece type | W | D | Length/ pcs. | velocity | Re |  | /piece | Total  | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - | g/s | m | m | m/s | - | - | - | - | mbar |
| DN50 pipe | 3.0 | 0.0553 | 4.37 | 4.07 | 55079 | 0.0246 | NA | 1.95 | 0.0494 |
| DN50 Elbow | 3.0 | 0.0553 | 6 | 4.07 | 55079 | NA | 0.203 | 1.22 | 0.0310 |
| CV-04 Valve | 3.0 | 0.0553 | 1 | 4.07 | 55079 | NA | NA | NA | 0.1956 |
| T-conn straight | 3.0 | 0.0553 | 1 | 4.07 | 55079 | NA | 0.04 | 0.04 | 0.0010 |
| Outlet | 3.0 | 0.0553 | 1 | 4.07 | 55079 | NA | 1.00 | 1.00 | 0.0254 |
| Total | 0.3024 |

He Supply branch line

Table 4.3 summarises the flow pressure drop calculation assumptions and results for the He Supply branch line. The calculation are done for density =129.72 kg/m3 and dynamic viscosity = 3.472.10-6 Pa.s  determined for T=4.5 K and p=3.0 bara from [5].

Table 4.3 Calculation assumption and results of the flow pressure drop in the He Supply branch line

| Piece type | W | L | D | Length/ pcs | Velocity | Re |  |  | Sum  | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | g/s | M | m | m | m/s | - | - | - | - | mbar |
| DN10 pipe | 3.0 | 3.455 | 0.0132 | 3.455 | 0.169 | 83349 | 0.0308 | NA | 8.05 | 0.1492 |
| Elbow | 3.0 | NA | 0.0132 | 6 | 0.169 | 83349 | NA | 0.20 | 1.20 | 0.0222 |
| T-conn branch | 3.0 | NA | 0.0132 | 1 | 0.169 | 83349 | NA | 0.91 | 0.91 | 0.0169 |
| CV-04 | 3.0 | NA | 0.0132 | 1 | 0.169 | 83349 | NA | NA | NA | 0.1530 |
| Inlet | 3.0 | NA | 0.0132 | 1 | 0.169 | 83349 | NA | 0.50 | 0.50 | 0.0093 |
| Total | 0.3505 |

TS Supply branch line

Table 4.4 summarises the flow pressure drop calculation assumptions and results for the TS Supply branch line. The calculation are done for density =17.236 kg/m3 and dynamic viscosity = 5.390.10-6 Pa.s  determined for T=35 K and p=12.8 bar a from [5].

Table 4.4 Calculation assumption and results of the flow pressure drop in the TS Supply branch line

| Piece type | W | L | D | Length/ pcs | Velocity | Re |  |  | Sum  | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | g/s | m | m | m | m/s | - | - | - | - | mbar |
| DN10 pipe | 4.5 | 3.9 | 0.0132 | 3.9 | 1.91 | 80531 | 0.031 | 9.10 | 9.100 | 2.855 |
| Elbows | 4.5 | NA | 0.0132 | 6 | 1.91 | 80531 | NA | 0.23 | 1.380 | 0.433 |
| T conn straight | 4.5 | NA | 0.0132 | 1 | 1.91 | 80531 | NA | 0.04 | 0.040 | 0.013 |
| Valve CV-60 | 4.5 | NA | 0.0132 | 1 | 1.91 | 80531 | NA | NA | NA | 3.813 |
| Inlet | 4.5 | NA | 0.0132 | 1 | 1.91 | 80531 | NA | 0.50 | 0.50 | 0.157 |
| Total | 7.270 |

TS Return branch line

Table 4.5 summarises the flow pressure drop calculation assumptions and results for the TS Return branch line. The calculation are done for density =10.73 kg/m3 and dynamic viscosity = 6.952.10-6 Pa.s  determined for T=55 K and p=12.5 bar a from [5].

Table 4.5 Calculation assumption and results of the flow pressure drop in the TS Return branch line

| Piece type | W | L | D | Length/ pcs | Velocity | Re |  |  | Sum  | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | g/s | m | m | m | m/s | - | - | - | - | mbar |
| DN10 pipe | 4.5 | 7.56 | 0.0132 | 7.56 | 3.05 | 62432 | 0.031 | 17.81367 | 17.814 | 8.947 |
| Elbows | 4.5 | NA | 0.0132 | 12 | 3.05 | 62432 | 0.031 | 0.23 | 2.760 | 1.386 |
| T conn straight | 4.5 | NA | 0.0132 | 1 | 3.05 | 62432 | 0.031 | 0.04 | 0.040 | 0.020 |
| T conn Branch | 4.5 | NA | 0.0132 | 1 | 3.05 | 62432 | 0.031 | 0.91 | 0.910 | 0.457 |
| Valve CV-61 | 4.5 | NA | 0.0132 | 1 | 3.05 | 62432 | 0.031 | NA | NA | 6.106 |
| Inlet | 4.5 | NA | 0.0132 | 1 | 3.05 | 62432 | 0.031 | 2 | 2.000 | 1.005 |
| Total | 17.821 |

## Total pressure drop in the main and branch cold process lines

Table 4.6 summarises the flow pressure drop for main and branch process lines as well as provides the maximum allowed pressure drop.

Table 4.6 Total pressure drop comparison with the maximum allowed pressure drop

| Line name | Main line press. drop | Branch line press. drop | Total press. drop | Max allowed press. drop |
| --- | --- | --- | --- | --- |
|  | mbar | mbar | mbar | mbar |
| VLP | 0.329 | 0.3024 | 0.6316 | 2.0 |
| He Supply | 0.621 | 0.3505 | 0.971 | 5.0 |
| TS Supply | 10.528 | 7.270 | 17.79 | 25 |
| TS Return | 17.109 | 17.821 | 34.93 | 35 |

From Table 4.6 it can be found that the calculated flow pressure drop in the all cold lines are lower than maximum specified ones.

## Auxiliary lines

The HP line and the Purge Return line will working at room temperature, therefore those lines are composed of linear and elbows pieces. The Helium recovery line will be equipped with the compensation bellows with internal sleeve, therefore, as in case of the cold process line, the flow pressure drop is calculated as for the linear pieces.

The assumptions and results of the flow pressure drop calculation in the auxiliary lines are presented in the Table 4.7. In the calculations the density and dynamic viscosity for each auxiliary lines is determined for the calculation pressure and the calculation temperature specified in Table 2.1.

Table. 4.7 Summary of the flow pressure drop calculation assumptions and results for 
SV Relief, HP, Purge Return and Helium Recovery lines

| Line name | Nominal diameter | Linear piec. total length | Elbow pcs. | Mass flow | Density | Viscosity | Total press. drop | Max allow. press. drop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | - | m | - | g/s | kg/m3 | 10-5 Pa.s | mbar | mbar |
| SV Relief line | DN100 | 63 | 17 | 50 | 0.171 | 1.993 | 15.57 | 50 |
| HP line | DN25 | 63 | 17 | 6 | 0.487 | 1.994 | 66.28 | 300 |
| Purge Return line | DN50 | 63 | 17 | 5 | 0.171 | 1.993 | 5.41 | 50 |
| Helium Recovery line | DN50 | 63 | 17 | 6 | 0.171 | 1.993 | 7.49 | 25 |

# Summary

Calculations of the flow pressure drop in the CDS-LTS2 cold process and auxiliary lines shows, that the size of the lines originally proposed by the ESS is correct.

# Reference

[1] ESS-0015216R1.1 - Technical Specification of the Cryogenic Distribution System for Lund Test Stand 2

[2] K. Jeżowiecka - Kabsch, H. Wójcik in "Mechanika płynów (Fluid mechanics)" - Oficyna Wydawnicza Politechniki Wrocławskiej 2001, ISBN 83-7085-597-0

[3] Dittmar N., Mickoleit E., Haberstroh Ch., Hesse U., Wolfram M., Krzyzowski M., Raccanelli A., " First Test Results on the Frictional Pressure Drop in Corrugated Tubes", Proceedings of the 13th Cryogenics 2014, IIR International Conference, April 7 - 11, 2014, Prague, Czech Republic, p. 225-229

[4] WrUT S_236_15 -103 - ESS CDS-LTS2 Control, manual and check valves sizing_R2.0

[5] HePak, Cryodata Inc.

# Comments

This value should be higher, since the mass flow rate from the CM can reach 104 g/s. See requirements ID2175 and ID2204.

How much higher will it be for 105 g/s?

For 105 g/s the pressure drop is 61.97 mbar