| European Spallation Source Cryogenic Distribution System for the Lund Test Stand2 Control, manual and check valves sizing |
| --- |
| Type of document | Technical document |
| ESS Contact Person | Jaroslaw FYDRYCH |
| WrUT references | S/263/15-103 |
| Version | 2.0 |
| Publication date | 2016.12.30 |

| Written by | Checked by | Approved by |
| --- | --- | --- |
| Jaroslaw POLINSKI | Jaroslaw POLINSKI |  |
| Signature: | Signature: | Signature: |

Revisions list

| Rev. No | Revision date | Revision scope |
| --- | --- | --- |
| 1.0 | 2016.12.16 | Original document |
| 2.0 | 2016.12.30 | Doc number is updated Changes provided after ESS comments from 2016.12.23 Correction in the CV-03 and CV-07 calculation by accounting the liquid flow through the valves |

Content

1.	Introduction	4

2.	Aim of the report	6

3.	Calculation teoretical background	8

4.	Calculation	9

4.1.	Calculation assumptions	9

4.2.	Calculation results	9

5.	Valve selection	10

6.	Reference	10

# Introduction

The CDS for Lund Test Stand 2 is dedicated to transferring cooling power from the TICP to the ESS elliptical cryomodules under their site acceptance tests in the test stand bunker. The system includes a cryogenic transfer line (CTL), one valve box and four auxiliary process lines.

The valve box is dedicated for the direct connecting of the tested cryomodules and controlling the helium flows in different operation modes. For these purposes it is equipped with a branch cryoline (so-called jumper connection) and a set of control valves.

Figure 1.1. The CDL for the LTS2 flow scheme

As shown in Figure 1.1 the valve box includes the following devices:

- 8 cryogenic control valves (CV03, CV04, CV06, CV07, CV60, CV61, CV63, CV64),

- 2 warm control valves (CV05 and CV62),

- check valve (NV60),

- 2 safety valves (SV02, SV60),

- 3 hand valve (HV01, HV60 and HV61),

- 2 pressure transmitters (PT01 and PT60),

- 4 temperature transmitters (TT05, TT06, TT60 and TT65).

Control valves CV03, CV04, CV60 and CV61 are for opening and closing the cold helium circuit and thermal shield circuit in the cryomodule. Two other cryogenic control valves, CV06 and CV63, as well as warm control valves CV05 and CV62 connect the cryomodule circuits to the helium recovery line and HP line, respectively. This set of valves is primarily used for warming up the tested cryomodule while keeping the TICP and CTL at 4.5 K stand by mode. During this phase the ambient temperature helium flows from the HP line into the cryomodule circuits and on to the helium recovery line, whilst cold helium flows from the helium supply and TS supply lines are reversed to the VLP and TS return lines via control valves CV07 and CV64.

Control valves CV05 and CV62 are used for flushing and purging the cryomodule circuits. During this operation, the valves allow filling the circuits with clean helium, while hand valves HV60 and HV90 direct the contaminated helium to the purge return line.

Warm control valves HV01 and HV61 are used for connection of the inert gas that is required for the welding of the helium and thermal shield circuits process pipes during cryomodule connection to the valve box.

# Aim of the report

The aim of the report is to select the proper size of the cryogenic control, warm control, hand and check valves. The valves operation conditions are provided in Tables 3, 6 and 7 of [1], and recall in this report in Tables 2.1 - 2.3 respectively.

Table 2.1. Cryogenic control valves in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | Tin K | m g/s | pin bar a | p mbar |
| --- | --- | --- | --- | --- | --- | --- |
| CV03 | cryogenic control valve, equal percentage, fail closed | Helium supply shut-off valve | 5.0 | 3.3 | 3.0 | 5.0 |
|  |  |  | 4.5-300 | 6.6 | 3.0 | 200 |
| CV04 | cryogenic control valve, equal percentage, fail open | VLP shut-off valve | 3.2 | 3.1 | 0.027 | 0.1 |
|  |  |  | 4.5-300 | 6.2 | 1.1 | 1 |
| CV06 | cryogenic control valve, equal percentage, fail closed | Helium recovery from VLP shut-off valve | 300 | 6.2 | 1.1 | 20 |
| CV07 | cryogenic control valve, equal percentage, fail closed | Helium supply-VLP control valve | 5.0 | 4 | 3.0 | 5.0 |
|  |  |  | 4.5-300 | 8 | 3.0 | 400 |
| CV60 | cryogenic control valve, equal percentage, fail closed | TS supply shut-off valve | 35 | 4.5 | 12.8 | 20 |
|  |  |  | 33-300 | 9 | 19.5 | 1000 |
| CV61 | cryogenic control valve, equal percentage, fail open | TS return control valve | 50 | 4.5 | 12.5 | 20 |
|  |  |  | 33-300 | 9.0 | 12.5 | 1000 |
| CV63 | cryogenic control valve, equal percentage, fail closed | Helium recovery from TS circuit shut-off valve | 33-300 | 9.0 | 2.0 | 500 |
| CV64 | cryogenic control valve, equal percentage, fail closed | TS supply-TS return control valve | 35 | 4.5 | 12.8 | 20 |
|  |  |  | 33-300 | 9.0 | 12.8 | 1000 |

Table 2.2. Cryogenic check valves in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | Tin [K] | m [g/s] | pin [bar] a | DP [mbar] |
| --- | --- | --- | --- | --- | --- | --- |
| NV60 | One-way check valve | Protection against overpressurization of the HP line | TBD | TBD | TBD | TBD |

a - all pressure values are given as absolute pressures

Table 2.3. Valves at ambient temperature in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | Tin K | m g/s | pin bar a | p bar |
| --- | --- | --- | --- | --- | --- | --- |
| CV05 | Control valve, equal percentage, fail closed | Controlling of warm helium flow from HP line to TS branch circuit | 300 | 6.4 | 3.0 | 0.5 |
| CV62 | Control valve, equal percentage, fail closed | Controlling of warm helium flow from HP line to helium supply branch line | 300 | 9.0 | 3.0 | 0.5 |
| HV01 | Shut off hand valve | Supply shielding gas for cryomodule installation | TBD | TBD | TBD | TBD |
| HV60 | Shut off hand valve | Opening TS branch circuit to Purge return line | 300 | 0.5 | 1.1 | 0.01 |
| HV61 | Shut off hand valve | Supply shielding gas for cryomodule installation | TBD | TBD | TBD | TBD |

# Calculation teoretical background

The flow coefficient of the valves is determined in accordance with [2].

## Compressible fluids

For compressible fluids the fluid flow through valve can have choked ed or non-choked ed character. If the condition:

(3.1)

where:

x - ratio of pressure differential across the valve to inlet absolute pressure (p/pin),

 - fluid isentropic expansion coefficient (specific heat ratio),

xT - valve type dependent constant - Table 2 [2],

is satisfied the flow has non-choke character, otherwise the flow is choked ed.

For the turbulent non-choked  flow of compressible fluids the valve flow coefficient kV can be calculated from:

(3.2)

where:

N6 - constant depend on the unit -  Table 1 [2]. In the calculations the N6= 31.6 for W[kg/h], p [bar a],  [kg/m3],

pin - fluid pressure at the valve inlet, bar a,

in - fluid density at the valve inlet, kg/m3,

Y - expansion factor:

.	(3.3)

For the turbulent choked  flow of compressible fluids the valve flow coefficient kV can be calculated from:

(3.4)

## Incompressible fluids

For incompressible fluids the ISA -75.01.01-2007 [2] also distinguish the choked or non-choked flow through a valve. If the condition:

(3.5)

where:

FL - liquid pressure recovery factor of a control valve without attached fittings,

pV - absolute vapor pressure of the liquid at inlet temperature, Pa,

pc - absolute thermodynamic critical pressure, Pa,

FF - liquid critical pressure ratio factor:

(3.6)

is satisfied the flow has non-choked  character, otherwise the flow is choked ed.

For the turbulent non-choked  flow of incompressible fluids the valve flow coefficient kV can be calculated from:

(3.7)

while, for the turbulent choked  flow

(3.7)

where

Q - Volumetric flow rate, m3/h

N1 - constant depend on the unit -  Table 1 [2]. In the calculations the N1= 1 for Q[m3/h], p [bar a]

0 - reference density 0 =1000 kg/m3

# Calculations

## Calculation assumptions

For the NV-60, HV-01 and HV-61 valves the operation conditions are not specified in [1] - compare Tables 2.2 and 2.3. Because the NV-60 check valve is in the same line as CV-62 valve the inlet temperature Tin and mass flow m should be identical as for the CV-62 valve - compare Figure 1.2. The inlet pressure at the 
NV-60 is taken as pin = 2.5 bar a by accounting the inlet pressure to the CV-62 (3.0 bar a) reduced by the pressure drop across this valve (p=0.5 bar). In the  present report the NV-60 check size is selected from a valve producer catalogue [3] based on the SE line size, then the pressure drop across the valve p is calculated hereafter.

For the HV-01 and HV-61 valves the Tin=300 K, pin=1.5, p=0.4 and mass flow m=0.9 g/s is assumed.

For CV-06 it is proposed to increase the p from 20 mbar to 25 mbar. It allows to keep the required mass stream through the valve and decrees the valve size in order to simplify the internal pipework design in the valve box and to decrees the heat flux to the cold pipes.

For the calculation purpose the valve type dependent constant xT=0.72 and liquid pressure recovery factor FL=0.9 are taken from Table 2 [2] for globe, single port, contoured plug valve where the flow tends to valve OPEN.

## Calculation results

Table 4.1 presents the specified/assumed data and calculation results of the minimum required valves flow coefficient.

Table 4.1. Specified /assumed data and calculation results of the minimum required valves flow coefficient

| Valve | Tin | pin | Fluid phase | p | W | G | x | Non-choked flow ? |  | in | Y | FF | kv |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | K | bar | - | bar | kg/h | m3/h | - | - | - | kg/m3 | - | - | m3/h |
| CV-03 | 300 | 3 | GAS | 0.2 | 23.76 | NA | 0.067 | YES | 1.666 | 0.487 | 0.974 | NA | 2.47 |
| CV-03 | 5 | 3 | LIQUID | 0.005 | NA | 3.3 | 0.001 | YES | 2,605 | 118 | NA | 0.69 | 0.489 |
| CV-04 | 300 | 1.1 | GAS | 0.001 | 22.32 | NA | 0.001 | YES | 1.667 | 0.179 | 1.000 | NA | 52.85 |
| CV-04 | 3.2 | 0.027 | GAS | 0.0001 | 11.16 | NA | 0.004 | YES | 1.684 | 0.417 | 0.999 | NA | 54.78 |
| CV-06 | 300 | 1.1 | 0.025 | 0.025 | 22.32 | NA | 0.022 | YES | 1.667 | 0.179 | 0.992 | NA | 10.61 |
| CV-07 | 300 | 3.0 | GAS | 0.4 | 28.8 | NA | 0.133 | YES | 1.667 | 0.487 | 0.948 | NA | 2.18 |
| CV-07 | 5 | 3.0 | LIQUID | 0.005 | NA | 4.0 | 0.001 | YES | 2,605 | 118 | NA | 0.69 | 0.593 |
| CV-60 | 300 | 12.8 | GAS | 1.0 | 32.4 | NA | 0.078 | YES | 1.664 | 2.068 | 0.969 | NA | 0.735 |
| CV-60 | 35 | 12.8 | GAS | 0.02 | 16.2 | NA | 0.001 | YES | 1.731 | 17.23 | 1.000 | NA | 1.235 |
| CV-61 | 300 | 12.5 | GAS | 1.0 | 32.4 | NA | 0.08 | YES | 1.665 | 2.020 | 0.968 | NA | 0.744 |
| CV-61 | 50 | 12.5 | GAS | 0.02 | 16.2 | NA | 0.002 | YES | 1.682 | 11.82 | 0.999 | NA | 1,055 |
| CV-63 | 300 | 2.0 | GAS | 0.5 | 32.4 | NA | 0.250 | YES | 1.666 | 0.325 | 0.902 | NA | 2.718 |
| CV-64 | 300 | 12.8 | GAS | 1.0 | 32.4 | NA | 0.078 | YES | 1.664 | 2.068 | 0.969 | NA | 0.735 |
| CV-64 | 50 | 12.8 | GAS | 0.02 | 16.2 | NA | 0.002 | YES | 1.682 | 12.09 | 0.999 | NA | 1,043 |
| CV-05 | 300 | 3 | GAS | 0.5 | 23.04 | NA | 0.333 | YES | 1.666 | 0.487 | 0.935 | NA | 1.580 |
| CV-62 | 300 | 3 | GAS | 0.5 | 32.4 | NA | 0.167 | YES | 1.666 | 0.487 | 0.935 | NA | 2.222 |
| HV-60 | 300 | 1.1 | GAS | 0.01 | 1.8 | NA | 0.009 | YES | 1.667 | 0.179 | 0.996 | NA | 1.352 |
| HV-01 | 300 | 1.5 | GAS | 0.4 | 3.24 | NA | 0.267 | YES | 1.666 | 0.244 | 0.896 | NA | 0.37 |
| HV-61 | 300 | 1.5 | GAS | 0.4 | 3.24 | NA | 0.267 | YES | 1.666 | 0.244 | 0.896 | NA | 0.37 |
| NV-60 | 300 | 2.5 | GAS | 0.2 | 32.4 | 9.0 | 0.080 | YES | 1.666 | 0.406 | 0.969 | 0.969 | 3,714 |

# Valve selection

Table 5.1 summarized the required flow coefficient for the particular valve and provides the valve producer and type. The CDS-LTS2 producer can select other manufacturer and the valves type, but the selection need to be done in respect of the min. required kV value, operation temperature and, in case of the cryogenic valves, heat transfer through the valve. It should be pointed out that selection of the other valve manufacturer would require minor modification of the CDS- LTS2valve box design.

Table 5.1. Required flow coefficient kV and election of producer and type of
 the cryogenic control, warm control, hand and check valves

| Valve | Required min kv | PN | DN | kv | Manufacturer/Type | Ref. |
| --- | --- | --- | --- | --- | --- | --- |
|  | m3/h |  |  | m3/h |  |  |
| CV-03 | 2.47 | 25 | DN10 | 2.8 | WEKA/Cryogenic Control | [4] |
| CV-04 | 54.78 | 25 | DN50 | 71 | WEKA/Cryogenic Control | [4] |
| CV-06 | 5.75 | 25 | DN20 | 11 | WEKA/Cryogenic Control | [4] |
| CV-07 | 2.18 | 25 | DN10 | 2.8 | WEKA/Cryogenic Control | [4] |
| CV-60 | 1.235 | 25 | DN8 | 2.0 | WEKA/Cryogenic Control | [4] |
| CV-61 | 1,055 | 25 | DN8 | 2.0 | WEKA/Cryogenic Control | [4] |
| CV-63 | 2.72 | 25 | DN10 | 2.8 | WEKA/Cryogenic Control | [4] |
| CV-64 | 1,05 | 25 | DN8 | 2.0 | WEKA/Cryogenic Control | [4] |
| CV-05 | 1.58 | 25 | DN8 | 2.0 | WEKA/ Warm Valve | [7] |
| CV-62 | 2.23 | 25 | DN10 | 2.8 | WEKA/ Warm Valve | [7] |
| HV-01 | 0.37 | 25 | 1/4 '' NTP | 0.388 | HOKE/1751M4Y | [6] |
| HV-60 | 1.36 | 25 | DN8 DN61) | 2.0 0.81) | WEKA/Cryogenic Control | [4] |
| HV-61 | 0.37 | 25 | 1/4 '' NTP | 0.388 | HOKE/1751M4Y | [6] |
| NV-60 | 3,72 | 25 | DN10 | 4.0 | WEKA/ CCV-33471 | [3] |

1) final size since kv value reduced as required by ESS [8]

# Reference

[1] ESS-0015216R1.1 - Technical Specification of the Cryogenic Distribution System for Lund Test Stand 2

[2] ISA -75.01.01-2007  (60534-2-1 Mod) - Flow Equations for Sizing Control Valves. International Society of Automation. 2007

[3] WEKA AG, CH-8344 Bäretswil, Switzerland, Cryogenic Check valve Type CCV /CCV-v, Catalogue 950421

[4] WEKA AG, CH-8344 Bäretswil, Switzerland, Cryogenic Valves, Specification no. 19911004

[5] WEKA AG, CH-8344 Bäretswil, Switzerland, Standard needle valves, chevro packing, Standard Line - 110

[6] HOKE, 1700 Series - Forged Body, Integral Bonnet Needle Valves

[7] WEKA AG, CH-8344 Bäretswil, Switzerland, Warm Valves, Specification No. 930115; Rev. 24.

[8] Jaroslaw Fydrych e-mail from 2016-07-21

# Comments

How much does the increased pressure drop affect time required for the cool-down and warm-up of a single cryomodule?

To be discussed during CDR

?

To be discussed during CDR

?

To be discussed during CDR

NV

NV

It is 60534-2-1 standard

Why is not EN 60534-2-1 used?