| European Spallation Source Cryogenic Distribution System for the Lund Test Stand2 Instrumentation list |
| --- |
| Type of document | Technical document |
| ESS Contact Person | Jaroslaw FYDRYCH |
| WrUT references | S/263/15-111 |
| Version | 2.0 |
| Publication date | 2016.12.31 |

| Written by | Checked by | Approved by |
| --- | --- | --- |
| Jaroslaw POLINSKI Piotr FELISIAK | Jaroslaw POLINSKI Maciej CHOROWSKI | Maciej CHOROWSKI |
| Signature: | Signature: | Signature: |

Revisions list

| Rev. No | Revision date | Revision scope |
| --- | --- | --- |
| 1.0 | 2016.12.16 | Original document |
| 2.0 | 2016.12.31 | Updated after ESS comments to CDR-LTS2 CDR charge |

Content

1.	Cryogenic control valves in the valve boxes of the CDS for the elliptical linac	4

2.	Pressure relief valves on the valve boxes of the CDS for the elliptical linac [1]	5

3.	Cryogenic check valves in the valve boxes of the CDS for the elliptical linac	5

4.	Control valves at ambient temperature in the valve boxes of the CDS for the elliptical linac	5

5.	Manual valves at ambient temperature in the valve boxes of the CDS for the elliptical linac	6

6.	Main vacuum isolation valve	6

7.	Insulation vacuum pressure transmitter	6

8.	Pressure transmitters in the valve boxes of CDL	7

9.	Temperature sensors in CTL	7

10.	Temperature sensors on the process lines in the valve boxes	8

11.	Temperature transmitters	8

12.	End switch	8

13.	Positioners for control valves in the valve boxes of the CDS for LTSt	9

14.	Automation cabinet 1 (AC1)	9

15.	Field distributor cabinet	9

16.	Reference	9

# Cryogenic control valves in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | PN | DN | Kv [m3/h] | Tmin [K] | Type/ Producer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CV03 | Control valve Equal percentage Fail to closed Pneumatic actuator | Helium supply shut-off valve | 25 | 10 | 2.8 | 4.0 | Cryogenic Control WEKA |
| CV04 | Control valve Equal percentage Fail to open Pneumatic actuator | VLP shut-off valve | 25 | 50 | 71 | 3.0 | Cryogenic Control WEKA |
| CV06 | Control valve Equal percentage Fail to closed Pneumatic actuator | Helium recovery from VLP shut-off valve | 25 | 15 | 5.8 | 4.0 | Cryogenic Control WEKA |
| CV07 | cryogenic control valve, equal percentage, fail closed | Helium supply-VLP control valve | 25 | 10 | 2.8 | 4.0 | Cryogenic Control WEKA |
| CV60 | Control valve Equal percentage Fail to closed Pneumatic actuator | TS supply shut-off valve | 25 | 8 | 2.0 | 30 | Cryogenic Control WEKA |
| CV61 | Control valve Equal percentage Fail to open Pneumatic actuator | TS return control valve | 25 | 8 | 2.0 | 30 | Cryogenic Control WEKA |
| CV63 | Control valve Equal percentage Fail to closed Pneumatic actuator | Helium recovery from TS circuit shut-off valve | 25 | 10 | 2.8 | 30 | Cryogenic Control WEKA |
| CV64 | cryogenic control valve, equal percentage, fail closed | TS supply-TS return control valve | 25 | 8 | 2.0 | 30 | Cryogenic Control WEKA |

# Pressure relief valves on the valve boxes of the CDS for the elliptical linac [1]

| Valve | Type | Function | PN | d0 [mm] | Tmin [K] | pset [bar g] | Type/ Producer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SV02 | Cryogenic pressure relief valve | Protection against overpressurization in helium supply line | 25 | 10 | 4.5 | 3 | Type 06855 HEROSE |
| SV60 | Cryogenic pressure relief valve | Protection against overpressurization in TS circuit | 25 | 10 | 33 | 24 | Type 06855 HEROSE |

# Cryogenic check valves in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | PN | DN | Kv [m3/h] | Tmin [K] | Type/ Producer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| NV60 | One-way check valve | Protection against overpressurization of the HP line | 25 | 10 | 4.0 | 283 | CCV-33471 WEKA |

# Control valves at ambient temperature in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | PN | DN | Kv [m3/h] | Tmin [K] | Type/ Producer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CV05 | Control valve Equal percentage Fail to closed Pneumatic actuator | Controlling of warm helium flow from HP line to TS branch circuit | 25 | 8 | 2.0 | 300 | Warm Valve WEKA |
| CV62 | Control valve Equal percentage Fail to closed Pneumatic actuator | Controlling of warm helium flow from HP line to helium supply branch line | 25 | 10 | 2.8 | 300 | Warm Valve WEKA |

# Manual valves at ambient temperature in the valve boxes of the CDS for the elliptical linac

| Valve | Type | Function | PN | DN | Kv [m3/h] | Tin [K] | Type/ Producer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| HV01 | Manual hand valve | Welding inner gas connetion in SC1 line | 25 | 1/4'' NTP | 0.388 | 300 | HOKE 1751M4Y |
| HV60 | Manual hand valve | Opening TS branch circuit to Purge return line | 25 | 6 | 0.8 | 300 | NV110 WEKA |
| HV61 | Manual hand valve | Welding inner gas connetion in SE line | 25 | 1/4'' NTP | 0.388 | 300 | HOKE 1751M4Y |

a - all pressure values are given as absolute pressures

b-to be confirmed by system manufacturer

# Main vacuum isolation valve

| Valve | Type | Function | DN | Producer | Type | Power consumption [W] |
| --- | --- | --- | --- | --- | --- | --- |
| PV70 | Maual valve | Opening the insulation vacuum envelop for vaccum pump station | DN100 | VAT Vacuum | Series 091 09140-PE08 | NA |

# Insulation vacuum pressure transmitter

| Pressure transmitter | Position | Pressure range [mbar abs] | Producer | Model | Output signal | Power consumption [W] |
| --- | --- | --- | --- | --- | --- | --- |
| PT70 | To monitor the insulation vacuum in the CDS | 1000 - 5×10-10 | Leybold vacuum | IONIVAC ITR 90 | 0-10V | >1.4 |

# Pressure transmitters in the valve boxes of CDL

| Pressure transmitter | Position | Pressure range [bar abs] | Producer | Model | Output signal | Power consumption [W] |
| --- | --- | --- | --- | --- | --- | --- |
| PT01 | helium supply branch line downstream CV03 | 0 - 12 | Emerson Rosemount | 3154NA | 4-20mA | 1.5 |
| PT60 | TS supply branch line downstream CV50 | 0 - 25 | Emerson Rosemount | 3154NA | 4-20mA | 1.5 |

# Temperature sensors in CTL

| Temperature transmitter | Position | Temperature range [K] | Installation | Redundancy | Producera | Modela |
| --- | --- | --- | --- | --- | --- | --- |
| TT11 | Helium supply line at the interface to the cold box | 4 - 300 | on pipe surface | YES | Lake Shore | CX-1070-SD-4L |
|  |  |  |  |  | Cryomagnetic Systems/ Temati | TVO |
| TT12 | VLP line at the interface to the cold box | 4 - 300 | on pipe surface | YES | Lake Shore | CX-1070-SD-4L |
|  |  |  |  |  | Cryomagnetic Systems/ Temati | TVO |
| TT13 | TS supply line at the interface to the cold box | 30 - 300 | on pipe surface | YES | TBD | PT-1000 |
| TT14 | TS return line at the interface to the cold box | 30 - 300 | on pipe surface | YES | TBD | PT-1000 |

a-to be disccused

# Temperature sensors on the process lines in the valve boxes

| Temperature transmitter | Position | Temperature range [K] | Installation | Redundancy | Producera | Modela |
| --- | --- | --- | --- | --- | --- | --- |
| TT05 | helium supply branch line in Jumper Connection | 4 - 300 | on pipe surface | NO | Lake Shore | CX-1070-SD-4L |
|  |  |  |  |  | Cryomagnetic Systems/ Temati | TVO |
| TT06 | VLP branch line in Jumper Connection | 4 - 300 | on pipe surface | YES | Lake Shore | CX-1070-SD-1.4L |
|  |  |  |  |  | Cryomagnetic Systems/ Temati | TVO |
| TT60 | TS supply branch line in Jumper Connection | 30 - 300 | on pipe surface | NO | TBD | PT-1000 |
| TT65 | TS return branch line in Jumper Connection | 30 - 300 | on pipe surface | NO | TBD | PT-1000 |

a-to be disccused

# Temperature transmitters

| Position | Producer | Model | Output signal | Power consumption [W] |
| --- | --- | --- | --- | --- |
| Automatics Cabinet1 | TBD | TBD | 4-20mA | ≈1.0 |

# End switch

| End switch | Position | Producer | Model | Detection signal | Output signal | Power consumption [W] |
| --- | --- | --- | --- | --- | --- | --- |
| ES60 | End switcher for HV60 | Namco | EA120 SPDT | Magnet EA120-10001 | 0-24V | <1.0 |

# Positioners for control valves in the valve boxes of the CDS for LTSt

| Name | Position | Producer | Model | Output signal | Power consumption [W] |
| --- | --- | --- | --- | --- | --- |
| Valve positioner without electronics board | Each control valve (8 for valve box) | Siemens | SIPART PS2 6DR5910–0NG00–0AA0 | NA | NA, powered by QRL module |
| QRL module - electronics for 5 positioners | 19’’ Drawer, Automation Cabinet, outside the radiation zone (2 for per valve box) | Siemens | QRL-AA A5E00252830 | Profibus PA | ≈1.0 |
| 19’’ Drawer for 2 QRL modules High - 2U; 88,1 mm Depth - 600 mm | Automation Cabinet, outside the radiation zone (1 item per valve box) | Siemens | A5E00250502 | NA | NA |

# Automation cabinet 1 (AC1)

Size:  TBD mm (Width × High × Depth)

# Field distributor cabinet

Size:  300 mm × 400 mm × 120 mm (Width × High × Depth)

# Reference

[1] J. Fydrych's e-mail "FW FW: SV02 and SV60 set pressures and relieving diameters" from 2016.01.05

# Comments

What are the flow characteristic (=%, linear) and rangeability (50, 100) of the control valves?

The flow type is already shown in table , column 2. The rangeability is as specified - not lower than 50.

SV80 is missing.

It should be PN 16 or higher.

It should be PN 25.

What are the flow characteristic (=%, linear) and rangeability (50, 100) of the control valves?

The flow type is already shown in table , column 2. The rangeability is as specified - not lower than 50.

It should be PN 16 or higher.

It should be PN 25.

It can be a hand valve, since it is not planned to have a vacuum pump connected permanently to the vacuum jacket pumping port.

PT71 is missing.

What is PY71?

It should be 0 -12. Refer to point 10 in https://ess-ics.atlassian.net/wiki/display/CDS/CDS-LTS2+baseline+documentation+changes.

It may be lower, down to 3.2 K.

Sensor calibration at temperature lower than 4K can generate an additional costs

It should be YES. Refer to Table 10 in the specification.