## Slide 1
D01, D03, E01, E02 Utilities and infrastructure
Gábor László
NSS Lead Instrument Engineer
10.09.2016

## Slide 2: Floor capacity and floor level in D01, D03, E01, E02.
Floor settlement requirement under the instruments
The floor in the experimental halls and bunker area will due to dynamics loading have a stability for elastic movement.: 3mm
Stability for creep/deformation over the lifespan of the facility: 3mm
Notes:   Energy
  Climate
  Health
  Agriculture
  Digital society

## Slide 3: Routing of the infrastructure
By the walls/pillars
From the galery
From the conduits
https://ess-ics.atlassian.net/wiki/display/SPD/CF+Info
Notes:   Energy
  Climate
  Health
  Agriculture
  Digital society

## Slide 4: 1. Nitrogen/Deionized water/Compressed Air/LAN
Nitrogen gas (10bar)
Deionized water (8 Bar)
Compressed air (6Bar)
LAN: 2 outlets/connections
Liquid nitrogen
1 filling point / sector
East and South Sector
14 connections from the galery and 7 on the wall.
North Sector
9 connections from the galery and 2 on the wall.
West sector
8 connections in E01 on the pillars+
1 at the bunker wall in D03.
No separate connection for W9-10.
Process flow chart: ESS-0046901, Layout: ESS-0046984
Notes:   Energy
  Climate
  Health
  Agriculture
  Digital society

## Slide 5: 2. Cooling water
East and South Sector (D01)
17 connections from the galery.
North Sector
9 connections from the D03 galery.
West sector
8 connections in E01 +
3 in E02 +
1 in D03 from the galery
Properties
7Bar, 8°C
Cooling capacity / average instrument: 27kW
Bunker
Separate cooling loops for each sector provided by ESS. Connections are by the beamlines.
(1 skid/sector, dedicated pipes for each instrument)
Process flow chart: ESS-0046901, Layout: ESS-0046984

## Slide 6: 3. Fume hoods and exhaust pipes for sample environments
East and South Sector (D01)
8 connections from the galery.
North Sector
5 connections from the D03 galery.
West sector
8 connections in E01
ESS-0056058, ESS-0048000, Layout: ESS-0046984

## Slide 7: 4. Tap and waste water
North Sector
1 water connection in D03 on the wall
1 drain to risk water system in D03
West sector
2 water connections in E01 on the wall +
2 in E02 on the wall + 1 in D03 on the wall
2 drains to risk water system in E01
2 drain to radiological waste water system in E02
East and South Sector (D01)
2 water connections in D01 on the wall
4 drains to risk water system in E01
Process flow chart: ESS-0046901, Layout: ESS-0055781, ESS-0055780, ESS-0046984

## Slide 8: 5. CF Power outlets
East and South Sector (D01)
2 connections from the galery and 20 on the wall.
North Sector
1 connection from the galery and 7 on the wall.
West sector
10 connections in E01 +
19 in E02 +
10 in D03
(Maximum distance : 18m)
Utilities power for installation and maintenance:
3pcs. 16A 1-phase outlets
1pcs. 16A 3-phase outlet
1pcs. 32A 3-phase outlet
Layout: ESS-0046984

## Slide 9: 6. Instrument Power distribution Concept /Preliminary/
Substation
Galery/Halls
Instrument distribution panel
/Main grounding zone./
Instrument distribution panel
/Grounding zone X/
Bunker distribution panel
/Bunker zone/
Lights
Motion
...
Chopper
Vacuum
Light
Detector
...
Motion
SAD
Instrument 1
Instrument 2
Instrument 3
Instrument 4
Instrument X
CF responsibity CF budget
NSS responsibity, Instrument budget
NSS responsibity, NSS budget

## Slide 10: 6. Instrument Power distribution Concept /Preliminary/
15
38
36
Bunker:
The bunker is a unified zone. There will be four distribution panels by D02 walls for the four sectors.
The design will be provided by ESS, the installation and material cost will be paid by the instruments. The design will be finalized according to the instrument designs.
There will be no central UPS system
The power distribution network will be planned according to our grounding rules.
All the missing insulation rules and solutions will be defined ASAP
Cave /Main zone/
There will be connection points similarly placed as the Sample environment connections
ESS Power and Grounding: ESS-0051373 (Not released)

## Slide 11: 6. Cabinet placement Concept /Preliminary/
Bunker:
We are planning to have cabinet arrays for each sector in order to minimize the cable lengths. The cabinets will be connected to the power distribution panel of the bunker sector. Also they will be connected to a common ICS router.
Constrains on cabinet placement:
Cable length limitations
Floorspace
Distance from sensitive components
Blocking of trafic routes including cranes
The cabinets should be outide of the shielding

## Slide 12: 7. ICS/DMSC Concept /Preliminary/
ICS/DMSC network will be provided by ESS. The network design will be finalized according to the instrument designs.

## Slide 13: 8. Additional infrastructure
Air conditioning
  Average temperature 22.0 ±2.0°C , No humidity requirement. No cooling only a ventilation system and heating.
Argon gas (Cylinder)
Helium gas (Cylinder)
Liquid Helium (Dewars)
  Liquefier and recovery (up to the collection point in the gallery)
Air conditioning: ESS-0056058, ESS-0048000

## Slide 14: 8. Cranes
D01 : ESS-0055303 (5ton), ESS-0055308 (7.5ton), ESS-0055305 (30ton)
D03 : ESS-0055307 (5ton), ESS-0055304 (7.5ton), ESS-0055306 (30ton)
E01 : ESS-0052338 (10ton)
E02 : ESS-0052339 (5ton)
E03, E04: ESS-0048477 (5/15 ton)
Mobile crane (preliminary): https://ess-ics.atlassian.net/wiki/display/SPD/Mobile+Cranes+in+E02
There will be mobile gantry cranes in E02 with 10ton capacity

## Slide 15: 9. Cranes

## Slide 16: 9. Jib cranes for sample area
LoKi Crane
CF has approved the mounting of the Lo-Ki Crane to D03 floor.
Arm length: 7m
Capacity: 1500kg.

## Slide 17: 9. Considerations for logistics inside the halls
General logistics: planning of logistics has started, comments are welcome:
https://ess-ics.atlassian.net/wiki/display/SPD/Logistics+in+D01%2C+D03%2C+E01%2C+E02
Crane logistics: Not analyzed in detail
Shielding logistics: Not analyzed in detail
Logistics for vehicle and personal traffic: Not analyzed in detail (,but)

## Slide 18: 9. Considerations for logistics inside the halls
Considerations for free path between the instruments and the building wall
Fire Safety path width: 0.9m
Size of vehicles: Truck (not oversized): 2.55m, 10 Ton forklift: 2.25 m.
Trucks will have dedicated loading areas at the bay doors. From these spots the goods will be transferred by forklifts or cranes.
Number and size of lanes (Free path rules)
  Strategy: Every instrument sample area has to be accessible by a 10Ton forklift with a maximum distance of 2m.
  There should be a possibility at every 60m where forklifts are able to overtake each other with proper visibility conditions. (Minimum width: 2.3m+2.3m+0.9m=5.5m, minimum length: 3x5.5m=16.5m).
  There should be a possibility at every 60m where forklifts can turn around /Right Angle Stacking Aisle/: width: 6.5m, length: 5m.
  One lane passages are possible between this places with a width of the maximum object size (see 4.): 3.6m.
  There is an option for narrow passage if both side of the place can be approached by a forklift with a 3.6m wide object, or if it is a dead-end. The width of the passage should be the width of a forklift plus 0.4m (2.7m). If there is a necessity for changing direction after the narrow passage (e.g.: corner of the building) the forklift should be able to turn safely: Length (loaded) 6m, Turning radius(outside): 3.9m.
  In case of the above-mentioned options the possible maneuvers has to be considered.
Maximum width of transported objects: door width-0.1m=3.6m
Landing and transfer spots has to be also considered

## Slide 19: Instrument Halls and labs
N
E03
E04
E01
E02
D03
D01
D02
D04
D08
Hall3
W1 NMX
W2 Beer
W3 C-Spec
W4 Bifrost
W5 Miracles
W6 Magic
W7 T-Rex
W8 Heimdal
E03
1 × Engineering
E04
1 × LS/SCM
1 × cold room
1 × instrument room
1 × Basic chemistry
1 × characterisation
Hall 1
E1 Estia
E7 Vespa
E8 Skadi
S2 Odin
S4 Dream
S11 Vor
D07
1 × LS/SCM
1 × cold room
D08
1 × Basic chemistry
Hall 2
N1 HR-NSE
N5 Freia
N7 Loki
D04
1 × LS/SCM
1 × cold room
2 × instrument room
Total = 14 + RML
Courtesy: P.Henry
D07

## Slide 20: E03
Level 100
Level 110
Loading Bay
Sample environment
Optics assembly
Slime

## Slide 21: E04
Level 100
Level 110
MCA
Detectors