Motion control and EPICS
Torsten Bögershausen
Motion Control and Automation Group
www.europeanspallationsource.se

---
Plans for today
- Overview
- EPICS abstraction
- Future development
- Demo of demo system
- Hands on

---
EPICS Training 2015 Using Motors
EPICS Training 2016 – short version
Using Motors
Stolen from Ronald L. Sluiter
2015-02-16
[Speaker Notes: Go to "View | Header and Footer" to add your organization, sponsor, meeting name here; then, click "Apply to All"]

---
What’s the Motor module for?
What’s the Motor module for?
Device independence – motor hardware is transparent to users.
  - Same user displays and motor motion behavior, for all devices.
Available operations from this display;
Make absolute or incremental moves.
Define the current position.
Stop the current move.
without any controller specific information.

---
Features - scope
Features - scope
- The scope of the MR is limited to single axis, non-coordinated, point to point moves.
- Including homing, status & error reporting
- Including the configuration of the axis (MRES, RDBD, HLM, LLM)
- Config good enough for “simple” motion controllers.
- Advanced motion controllers have many, many more parameters
- My plan is to change the configuration for ESS:
  read values from controller and put them into the MR
- The scope for the model 3 driver is larger:
- For multi-axis coordinated motion and trajectory scans see…
  - https://subversion.xray.aps.anl.gov/synApps/motor/trunk/documentation/trajectoryScan.html

---
Features - coordinate systems.
Features - coordinate systems.
steps or ticks
Raw
EGU’s
Dial
User
X
RVAL
MRES
DIR: +/- 1
OFF
X
DVAL
VAL
+

---
Feedback data flow
Feedback data flow
ERES
MRES
RMP
DIR: +/- 1
UEIP = URIP = No, OR,
URIP = Yes
UEIP = Yes
+
UEIP = Yes
X
X
DRBV
RRBV
RBV
REP
OFF
÷
MRES
RDBL Link
X
RRES
UEIP = URIP = No
URIP = Yes

---
Features – Move types
Features – Move types
- Absolute (VAL, DVAL, RVAL)
- Relative (RLV)
- Incremental (TWF, TWR, TWV)

---
MotorRecord @ ESS
- Abstracts the motor into an EPICS PV
  LabS-ESSIIP:MC-Pos-01
  LabS-MCAG:MC-Pos-TS01
- Converts writing to a field into commands
  to the controller
- Retrieves the status from the controller
- EPICS PV can be reached via:
- C/C++/Java/Python/sh

---
Fields used in motorRecord
- VAL: Where the motor should be
- RBV: Where the motor is
- MOVN: Moving
- DMOV: Done moving
- STOP: stop moving
- LVIO: (soft) limit violation
- STAT: Alarm status
- MISS: ”Missed” (see RDBD, ”retry deadband”)

---
Limitations in motorRecord
- Stepper motor abstraction
  - No good support for microstepping
  - No good support for controllers using EQU, e.g. Millimeter
- Features, which are considered a ”bug” today: motor stopped when
  going into the wrong direction
- But: a usable abstraction of a motor

---
MotorRecord today
- Maintained at APS.
- Issue(s):
  Change one line of code -> something breaks on another beamline
- Solution:
  a) Take out a new branch to work on
  b) Clean up, refactor & develop
  c) Keep most EPICS fields, remove some
  d) Result is no more 100% ”the motorRecord”
  e) As agreed with APS, call it ”axisRecord”

---
AxisRecord
- Ongoing development under 2017++
- Deployed at ESS early 2017
- caget(motor.RBV) works as before.

---
Status as used at SNS
3 States in control screen:
IDLE Moving ERROR
if (!DMOV || MOVN)
 status = Moving
else if (STAT != 0 || MISS)
 status = ERROR
else
 IDLE

---
Status as used in Nicos ?
4 States in control screen:
OK BUSY WARN ERROR
if (!DMOV || MOVN)
 status = BUSY
else if (LVIO)
 status = WARN
else if (STAT != 0 || MISS)
 status = ERROR
else
 status = OK

---
Motion Control Integration (today)
Motion Control Integration (today)
3 layers in control box:
EPICS IOC
Motor record (single axis)
Model 3 driver
Basic functionalities for point-to-point movements
Future extensions of functionality in additional records
CSS BOY
caget / caput
Instrument Control (e.g. Python based)
EPICS Control Network
Channel Access
IOC: EPICS (base)
MotorRecord
m1
Model 3 driver
Ethernet + TCP/IP
Motion Control Unit
Encoder
Motor
(End) switches

---
Motion Control Integration (tomorrow)
Motion Control Integration (tomorrow)
3 layers in IOC:
Motor record (single axis)
longout record (homing)
Model 3 driver
Basic functionalities for point-to-point movements
Future extensions of functionality in additional records
Current development includes a.o. jerk, homing procedures
Extensions need to be implemented in user interfaces, model 3 driver and motion control unit as well (strong coordination necessary)
CSS BOY
caget / caput
Instrument Control (e.g. Python based)
EPICS Control Network
Channel Access
IOC: EPICS (base)
 MotorRecord
m1
 longout
m1-PrcHom
Model 3 driver
Ethernet + TCP/IP
Motion Control Unit
Encoder
Motor
(End) switches

---
Move & monitor a motor
Move & monitor a motor
(done on a simulator, Mac or raspi)
- camonitor IOC:m1.RBV IOC:m1.DMOV
- IOC:m1.RBV 2016-02-02 10:58:16.157350 24.87
- IOC:m1.DMOV 2016-02-02 10:58:16.658745 1
- IOC:m1.DMOV 2016-02-02 10:58:16.658745 0
- IOC:m1.RBV 2016-02-02 10:58:30.124368 49.86
- IOC:m1.RBV 2016-02-02 10:58:31.138087 60.06
- IOC:m1.DMOV 2016-02-02 10:58:31.639072 1
- caput IOC:m1.VAL 60.1
- Old : IOC:m1.VAL 24.9
- New : IOC:m1.VAL 60.1
#Notes:
#caput: Channel access put
#camonitor: Channel access monitor
#IOC:m1..DMOV: Field “done moving”
#IOC:m1.RBV: Field Read back value

---
Automated tests
- Find many bugs
- Python based
- With real hardware
- Today: Part of TwinCAT,
  Tomorrow: Part of axisRecord.

---
python
- motor = 'LabS-ESSIIP:MC-Pos-01'
- epics.caput(motor, destination, wait=True)
- stat = epics.caget(motor + '.STAT', use_monitor=False)

---
Future plans
- Tomorrow: EPICS driver part of axisRecord
- Today: Configuration MR → controller
- Tomorrow: Configuration controller → MR
- Slits as virtual axes
- Scans as waveforms

---
Motion at in kind partners
- ISIS ?
- JCNS ?
- PSI ?
- Other ?

---
Requirements
- Positioner – single axis
- Coordinated slit
- (wire) scan & position capture
- What more ?

---
Tools
- Git – version control
- Jira – issue tracker
- Naming convention !
- CCDB – IOC factory
- How do you store low level motor configs ?
  Mark ? Fabian ? ISIS ? Others ?
  /home/motion/BEAMLINE1/motor1
  LabS-ESSIIP:MC-Pos-01

---
SW platforms
- TwinCAT
- Linux open source
- Simulator in C (volonteers for python ?)
- Test code in python
  Function test for the Record
  Commisioning real hardware

---
EPICS interface
- motor Record ->axis Record
- Profile move
- Position readback (arrays == waveforms)
- RPC with ”EPICS7” ?

---
That's it – in theory
Questions ?

---
Hands on
- Start your VM

---
That's it
Thanks for listening