## Slide 1: STATUS OF CRYOGENIC HAZARD AT ESS SINCE ESHAC#3
D.Phan with the contribution of S.Birch, E.Lundh, J.Fydrych, IK-partners and others
ESHAC#5 – 3rd and 4th October 2016
Contact: duy.phan@esss.se

## Slide 2
AGENDA
Status of the ESS ODH Safety process and implementation ESS-0038692
Results and lessons learnt from the Computational Fluid Dynamics (CFD) simulations in the accelerator tunnel
Safety studies and concept against Oxygen Deficiency Hazard in the accelerator buildings
1
2
3
Upcoming activities and challenges
4

## Slide 3
February 2016
Acknowledgement : R.ERIKSSON
Helium Compressor building (HCB)
Klystron Gallery (KG)
Accelerator Tunnel (AT)
Introduction
View of the accelerator buildings
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Coldbox Building (CXB)
Gallery Technical Area (GTA)

## Slide 4
ESS has developed an ODH safety process for the accelerator which is based on regulatory requirements; the DRAFT has been circulated in May, 2015, and the revised version will be approved by ES&H. The concept will be expanded to all ODH areas at ESS.
ESS shall consider starting the modeling of the premises in order to carry CFD simulations on cryogenic spills, fire risk assessment as well as air/smoke management. […]
As part of the CFD analysis, ESS should pay particular attention to the elevated section at the end of the accelerator tunnel.
1
2
ESHAC – Environment, Health and Safety Advisory Committee June 2015
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 5
ODH Safety process & implementation
Overview and progress
Objectives
- Enforcement of the ODH safety process at ESS
- Description of the following:
  Applicable rules (EU, Swedish, ESS)
  ODH calculation methodology
  List of control measures (training, PPE, ventilation, etc.)
  Cryogenic Safety Committee
  Content of the Safety File
ESS wide
ESS-0038692
Mainly inspired by
FESHM 4240: Oxygen Deficiency Hazard
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
HANDED OVER TO ES&H DIVISION IN FEBRUARY 2016

## Slide 6
ODH Safety process & implementation
Example of implementation
1
2
Accelerator buildings
ODH assessment
Safety support for ODH assessment
3
Control measures
Control measures
4
Review & approval
September 16th 2016
Area responsible
ODH detection
Cryo. Safety Review Committee
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 7
Objectives
Collect missing information for ODH studies
Discuss the failure scenarios chosen for the on-going ODH assessments
Tailor the ODH safety process & strategy to ESS’ needs
Discuss the implementation of control measures such as ventilation, training, etc.
Frequency: once every 2 months
Working Group:
1 representative from AD RP & Safety
1 representative from Cryomodules
1 representative from Cryogenics
1 representative from ES&H
1 representative from ICS
1 representative from Target Safety
1 representative from Science
5 Sessions carried out so far
ODH working group
Overview
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 8
Results from the preliminary ODH assessment ESS-0063324
Most credible accidental scenario
sudden loss of the beam vacuum leading to the release of the full helium inventory from one cryomodule (e.g. rupture of one of the power coupler ceramic windows)
Ground surface | Height | Volume | Temperature | Pressure | Ventilation rate
3600 m2 | 3.5 m | 12 600 m3 | 18°C | 1 atm | 25 200 m3/h
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 9
Results from the preliminary ODH assessment ESS-0063324
Step 1: steady-state calculation model
Fluid | State | Volume | Operational pressure | Temperature
Helium (High-β elliptical cryomodule) | Liquid | 0.226 m3 | Max 1.43 bara | 2 K
Volume of gas discharged: 203 m3
O2 in the air after discharge: 20%
Special case: due to the particular geometry (low height and presence of a dead-end in the A2T area) of the tunnel and the numbers of helium discharge points in the tunnel, it was decided to perform a CFD simulation in order to estimate the temperature, the oxygen concentration as well as the pressure evolution at various locations and times in the tunnel in case of a release of helium
ODH CLASS 0
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 10
Emergency exits
HEBT entrance (chicane)
FEB entrance (chicane)
Overview
A2T egress
135 m
133 m
130 m
132 m
51 m
Accelerator tunnel
Layout of the ODH monitoring system
Acknowledgement : S.BIRCH
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 11
Accelerator tunnel
Layout of the ODH monitoring system
Acknowledgement : S.BIRCH
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Accelerator tunnel 14 x 4 port Oxigraf Model O2iM oxygen deficiency Monitors mounted at high level.
Accelerator Tunnel exits and entrances 6 x 1 port Oxigraf Model O2iM oxygen deficiency Monitors mounted at high level.
50 Accelerator Beam Off Stations + 30 strobes and sirens.
Stub

## Slide 12
Accelerator tunnel
Safety issue in the A2T area
51 m to the nearest exit
219 m to the last cryomodule
Acknowledgement : N.GAZIS
64 seconds (30+34) to reach the nearest exit
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 13
Accelerator tunnel
Safety issue in the A2T area
Acknowledgement : N.GAZIS
Decision taken on December 2015 to implement a safety hatch in the A2T area
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 14
Discharge of GHe through the 2 rupture disks located on the LHe line (1,9 s)
Loss of the content of 1 High-β* cryomodule (28,4 kg at 2 K and 2.04 bara)
Accelerator tunnel
CFD simulations
Failure scenarios considered (during access)
Scenario 1
Rupture of the power coupler’s window or beam line
Max. mass flow rate = 15,2 kg.s-1
Acknowledgement : J.P THERMEAU – WP5_SAFETYSIZING_SAFETY_DEVICES
*the loss of 2 High-Beta cryomodules has not been considered thanks to the CLOSE position of the gate valves in-between cryomodules during access
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 15
Accelerator tunnel
CFD simulations
Failure scenarios considered (during access)
Scenario 2
Rupture of the insulation vacuum vessel of 1 High-β cryomodule
Loss of the content of 1 High-β* cryomodule (28,4 kg at 2 K and 2.04 bara)
Discharge of GHe through the 2 rupture disks located on the LHe line (11,8 s)
Max. mass flow rate = 2,4 kg/s
*the loss of 2 High-Beta cryomodules has not been considered thanks to the CLOSE position of the gate valves in-between cryomodules during access
Acknowledgement : J.P THERMEAU – WP5_SAFETYSIZING_SAFETY_DEVICES
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 16
Accelerator tunnel
CFD simulations
Scenario 1 (15.2 kg.s-1 during 2 s) – rupture of the beam line
ESS Threshold
Acknowledgement : E.LUNDH
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 17
Accelerator tunnel
CFD simulations
Mass flow rate: 2,4 kg.s-1
Mass: 28,4 kg
Leak duration: 12 s
Location: contingency space (A2T area)
Ventilation mode: ON – 25 200 m3/h
Mass flow rate: 2,4 kg.s-1
Mass: 28,4 kg
Leak duration: 12 s
Location: contingency space (A2T area)
Ventilation mode: OFF
ESS Threshold
ESS Threshold
Acknowledgement : E.LUNDH
Scenario 2 (2.4 kg.s-1 during 2 s) – rupture of the vacuum vessel of a High-β
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 18
Accelerator tunnel
CFD simulations – Preliminary conclusions
A2T area
Implementation of a safety hatch in the A2T area to facilitate evacuation
 The minimum time needed to reach the nearest exit from the A2T area (64 seconds) does not allow a safe evacuation
1
Reinforcement of the hinges and frame of the emergency exit doors
 The force applied on the doors in case of a failure of a cryomodules would be around 50 kN.m-2 (500 kg.m-2)
2
Investigation on compensatory measures close to the discharge points (e.g. helium collection header)
Lowest attainable O2 concentration = 6%
Lowest attainable temperature = -135°C
3
Safety hatch
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 19
ESS Cryogenic Safety Workshop February 10-11, 2016
Highlights
7 institutes represented
2-days workshop
10 recommendations addressed to ESS
Presentations available here: https://indico.esss.lu.se/event/438/
Objective: share experience and technical expertise with cryogenic and safety experts regarding cryogenic safety in accelerator tunnels
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 20
ESS Cryomodules Safety Review June 9, 2016
Highlights
Presentations and report from the committee available here: https://indico.esss.lu.se/event/542/
Objective: evaluate the design of the Spoke and Elliptical
cryomodules against failures and risks to humans and equipment during operation
The design of the collector is however still in a preliminary state, and it is was not possible for the committee to review the solution in depth. The committee supports the continuation of this work with high priority, as well as the evaluation of the impact of this system on the cryomodule design and integration aspects in the tunnel.
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction

## Slide 21
ESS ODH Safety Review September 16, 2016
Highlights
Presentations and report from the committee available here: https://indico.esss.lu.se/event/625/
Objective:
Review the ODH scenarios of the accelerator buildings (relevancy, calculation model, etc.)
Review the strategy and layout of the ODH monitoring system
Advice on control measures to be put in place to guarantee the safety of the activity/equipment/installation
Provide a formal recommendation on whether the ODH monitoring system should proceed to procurement and installation phases
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction

## Slide 22
ESS ODH Safety Review September 16, 2016
Top 5 recommendations
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction
The methodology presented to assess ODH is globally satisfying and seems to be adequate and rather complete but a complementary evaluation of the evacuation time in the event of a helium/nitrogen release should be performed for each accelerator building in order to identify potential additional control measures.
1
2
ESS should re-evaluate the needs to carry personal oxygen monitors in each building potentially subject to oxygen depletion.
In case of on an ODH event, the cryogenic and main control room will be informed upon trigger of the ODH detection system but there is no formal ESS emergency procedure at the moment. Therefore ESS, in particular ES&H Division, needs to clarify as soon as possible the alert procedure of the rescue team in the event of an ODH.
3

## Slide 23
ESS ODH Safety Review September 16, 2016
Top 5 recommendations
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction
Efforts should be made to align the ODH and fire alarms and strobe lights, and to reduce the number of lights of the beam-off stations in order not to confuse the operators in case of an emergency situation, especially in the accelerator tunnel. In the same context, ESS should also consider implementing evacuation push buttons in the accelerator tunnel in order to manually trigger the evacuation in case of an ODH event.
4
5
The review committee acknowledges the decision to have ODH monitors with multiport sampling in the accelerator tunnel but recommends also considering the implementation of ODH monitors with fast sampling (single port) and a longer distance between monitors as well as reducing the number of sirens/strobes which might has been overestimated.

## Slide 24
Accelerator tunnel
Conceptual design of the Helium collection header
Flap valve in CLOSED position
Gate valve in CLOSED position
Gate valve in CLOSED position
Gate valve in CLOSED position
Access Mode
Most credible accidental scenario: loss of one High-β cryomodule
7.25 kg/s
7.25 kg/s
Flap valve in CLOSED position
Flap valve in CLOSED position
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction

## Slide 25
Accelerator tunnel
Conceptual design of the Helium collection header
Flap valve in OPEN position
Gate valve in OPEN position
Gate valve in OPEN position
Gate valve in OPEN position
Beam Mode
Most credible accidental scenario: loss of six High-β cryomodules
7.25 kg/s
7.25 kg/s
7.25 kg/s
7.25 kg/s
Proton beam
Flap valve in OPEN position
Flap valve in OPEN position
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction
Design report expected for mid-November

## Slide 26
Accelerator tunnel
Conceptual design of the Helium collection header
CDS vent line
310 m
Cold box room vent line
CTL gallery
L = 55 m
Accelerator tunnel
Total length of the collector < 400 m
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction
Acknowledgement : J.FYDRYCH

## Slide 27
Accelerator tunnel
Conceptual design of the Helium collection header
1
2
Location 1 – clashes with the CM vacuum pumping units;
difficulties in the CM installation
Location 2 – clashes with the valve box side process lines;
difficulties in repair and maintenance work on valve box
Acknowledgement : J.FYDRYCH
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction

## Slide 28
?
ANY QUESTIONS
Contact: duy.phan@esss.se

## Slide 29
BACK-UP SLIDES

## Slide 30
Accelerator tunnel
CFD simulations
GHe released at 5 K (coldest value from the designer)
Constant mass flow rates from the burst disks
Atmospheric pressure in the tunnel
100% leak tightness in the tunnel
Walls and equipment held at a constant temperature of 22.5 °C
Constantly forced ventilation (about 0.3 – 0.4 m.s-1 in the tunnel)
Simplified geometry
CDS and cryomodules installed in the contingency space
Cryogenic helium properties from the NIST Chemistry WebBook
The simulation software CFX (ANSYS) is used
Assumptions
Acknowledgement : E.LUNDH
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 31
Introduction
View of the accelerator buildings (3D model)
Helium Compressor building (HCB)
Cryogenic Transfer Line Gallery (CTLG)
Gallery Technical Area (GTA)
Accelerator Tunnel (AT)
Acknowledgement : N.GAZIS
TS2 bunker
Target Moderator CryoPlant Hall (TCH)
Accelerator CryoPlant Hall (ACH)
High Pressure Gas Storage (HPGS)
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Coldbox Building (CXB)

## Slide 32
Accelerator tunnel
Conceptual design for the air management system
Proton beam
Fire damper
Air supply
Air exhaust
O2
O2
O2 detector – Oxigraf 4 port multiport sampling (laser diode technology)
O2
O2
O2
ODH is not relevant during beam operation
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 33
Accelerator tunnel
Conceptual design for the air management system
If a Helium discharge occurs, it will be partly handled by the ventilation system…
≈140 hours of maintenance/year
Lesson learnt from CERN’s visit (2 July 2015)
 air speed from the ventilation should not exceed 1 m.s-1 to facilitate evacuation
Air supply
Air exhaust
O2
O2
O2
O2
25 200 m3/h
25 200 m3/h
O2
O2
O2
O2
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 34
Accelerator tunnel
ODH studies – CFD simulation of helium discharge
Acknowledgement : E.LUNDH
Temperature and O2 concentration need to be evaluated locally (close to the He discharge points) as well as pressure rise
Assessment of human evacuation (pathway, time) in case of a helium release
Help in the decision-making to CF for the design of the ventilation system
Help in the definition of the access procedure to the LINAC (warm-up, cool-down, steady-state)
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 35
Accelerator tunnel
Proposed control measures
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges
Introduction
Technical Safety measures
Warning signs
Fixed area oxygen monitoring with audible alarm(s) and flashing light(s)
Safety hatch in the A2T area to facilitate evacuation in case of ODH event
Feasibility study of a helium collection header connected to the burst disks of the CM
Organizational Safety measures
ODH training (e-learning)
Closing of the gate valves located in-between the CM prior to any access to the accelerator tunnel
Personal oxygen monitors
Presence of minimum two persons
Administrative Safety measures
Access restricted to authorized personnel only
Emergency procedure
Access procedure
Working procedure

## Slide 36
Access to the installations (north) tunnel wall is possible under the DTL
Access to the installations (north) tunnel wall could be possible under the LEBT/RFQ/MEBT (t.b.d.)
Accelerator tunnel
Integration and Verification – Warm linac
Acknowledgement : N.GAZIS

## Slide 37
Access to the installations (north) tunnel wall is possible under the LWU (through the LWU support table)
Temporary ladders can be installed on top of the LWU for access around it
SPK CM do not allow for access route to the installations (north) tunnel wall
Accelerator tunnel
Integration and Verification – Spoke
Acknowledgement : N.GAZIS

## Slide 38
Accelerator tunnel
Integration and Verification – Medium and High-β Linac
Access to the installations (north) tunnel wall is possible under the LWU (through the LWU support table)
Temporary ladders can be installed on top of the LWU for access around it
Acknowledgement : N.GAZIS

## Slide 39
Access to the installations (north) tunnel wall is facilitated throughout HEBT, Dog-Leg and A2T
Accelerator tunnel
Integration and Verification – HEBT, Dog-Leg and A2T

## Slide 40
Accelerator tunnel
CFD simulations
Failure scenarios considered (during access)
Scenario 3
Helium leakage from the VLP line in the insulation vacuum of the Cryogenic Distribution System (CDS)
Discharge of GHe through the pressure relief device on the insulation vacuum jacket (4 s)
Max. mass flow rate = 15 kg/s
Loss of the content of the CDS in the contingency space (60 kg at 3 K and 6 bara )
Acknowledgement : J.FYDRYCH

## Slide 41
Accelerator tunnel
CFD simulations
Mass flow rate: 2,4 kg.s-1
Volume: 28,8 kg
Leak duration: 12 s
Location: contingency space (A2T area)
Orientation of the burst disks: towards IS
Mass flow rate: 2,4 kg.s-1
Volume: 28,8 kg
Leak duration: 12 s
Location: contingency space (A2T area)
Ventilation mode: towards target
ESS Threshold
ESS Threshold
Acknowledgement : E.LUNDH
Scenario 2 (2.4 kg.s-1 during 2 s) – rupture of the vacuum vessel of a High-β

## Slide 42
Nearest exit from the A2T
Discharge point
A
C
B
Ventilation ON
25 200 m3/h
Accelerator tunnel
CFD simulations
Scenario 2 (2.4 kg.s-1 during 2 s) – rupture of the vacuum vessel of a High-β
Notes: Punkter I mitten av gången….Ska bara visa resultat från de närmsta punkterna, de 15 m bakåt och närmsta exit från A2T
Punkterna är på 0.5m, 1.75m och 3m

## Slide 43
A
Ventilation ON
25 200 m3/h

## Slide 44
B
Ventilation ON
25 200 m3/h

## Slide 45
C
Ventilation ON
25 200 m3/h

## Slide 46
Discharge of GHe through the 2 rupture disks located on the LHe line (1,9 s)
Loss of the content of 1 High-β* cryomodule (28,4 kg at 2 K and 2.04 bara)
Accelerator tunnel
CFD simulations
Failure scenarios considered (during access)
Scenario 1
Rupture of the power coupler’s window or beam line
Max. mass flow rate = 15,2 kg.s-1
Acknowledgement : J.P THERMEAU – WP5_SAFETYSIZING_SAFETY_DEVICES
P
Air inlet
P
P
P
Q
Q
Q
Q
*the loss of 2 High-Beta cryomodules has not been considered thanks to the CLOSE position of the gate valves in-between cryomodules during access
Introduction
ESS ODH Safety process and implementation
Results from CFD simulations
ODH in the accelerator tunnel
Upcoming activities and challenges

## Slide 47
Accelerator tunnel
CFD simulations
Acknowledgement : E.LUNDH
Scenario 3 (15 kg.s-1 during 4 s) – rupture of the VLP line

## Slide 48: Accelerator tunnel CFD simulations
Geometry
Notes: Berätta att geometrin har ändrats
Orientation of the burst disks…

## Slide 49: Accelerator Air Management System On-going Safety studies
CFD Project Request
Hazardous scenarios
Tunnel dimensions and characteristics
Environmental conditions
Description of the cryogenic circuit
Description of the cryomodules
Leak, abrupt rupture, discharge from safety device, etc.
Length, width, height, internal volume, helium escape routes, etc.
Pressure and temperature in the tunnel
Mass of helium, operating pressure and temperature, safety device, etc.
Mass of helium, operating pressure and temperature, safety device, etc.
Description of the HVAC system
Ventilation rate, location of the air inlet and outlet, etc.
Objective: Define the boundary conditions necessary for the CFD simulation
Responsibility: Accelerator Division
Time frame: finalized

## Slide 50: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.5 | 1.0 | 5.0 | 10.0 | 15.0 | 30.0 | 60.0
Oxygen concentration | 0.21 | 0.20383 | 0.20199 | 0.20205 | 0.20211 | 0.20261 | 0.20318 | 0.20371 | 0.20506 | 0.20696
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 1: full length – normal ventilation
600 m
Volume available: 4410 m3
Ventilation rate: 12 600 m3/h (1 ACH)
During release:
After release:
Acknowledgement : N.GAZIS (ESS)

## Slide 51: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.5 | 1.0 | 5.0 | 10.0 | 15.0 | 30.0 | 60.0
Oxygen concentration | 0.21 | 0.18394 | 0.17666 | 0.18 | 0.18301 | 0.19842 | 0.20598 | 0.20861 | 0.20994 | 0.21
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 2: section between 2 exits – normal ventilation
135 m
Volume available: 992 m3
Ventilation rate: 12 600 m3/h (1 ACH)
1,2 s
31,2 s after the release started
02 ≥ 18%
02 < 18%
During release:
After release:
Acknowledgement : N.GAZIS (ESS)

## Slide 52: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.5 | 1.0 | 5.0 | 10.0 | 15.0 | 30.0 | 60.0
Oxygen concentration | 0.21 | 0.18394 | 0.17666 | 0.18133 | 0.18535 | 0.20265 | 0.20838 | 0.20964 | 0.21 | 0.21
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 3: section between 2 exits – 1 smoke extractor*
135 m
1,2 s
22,3 s after the release started
02 ≥ 18%
02 < 18%
During release:
After release:
*considering a quasi-immediate trigger of the smoke extraction
Volume available: 992 m3
Ventilation rate: 18 000 m3/h (1,4 ACH)
Acknowledgement : N.GAZIS (ESS)

## Slide 53: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.5 | 1.0 | 5.0 | 10.0 | 15.0 | 30.0 | 60.0
Oxygen concentration | 0.21 | 0.18394 | 0.17666 | 0.18535 | 0.19178 | 0.20838 | 0.20992 | 0.21 | 0.21 | 0.21
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 4: section between 2 exits – 2 smoke extractors*
135 m
Volume available: 992 m3
Ventilation rate: 36 000 m3/h (2,8 ACH)
1,2 s
11,5 s after the release started
02 ≥ 18%
02 < 18%
During release:
After release:
*considering a quasi-immediate trigger of the smoke extraction
Acknowledgement : N.GAZIS (ESS)

## Slide 54: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.1 | 0.3 | 0.4 | 0.52166 | 0.7 | 2.0 | 5.0
Oxygen concentration | 0.21 | 0.18394 | 0.17666 | 0.17671 | 0.17683 | 0.17689 | 0.17697 | 0.1787 | 0.18887 | 0.20147
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 5: section between 2 exits – 1 smoke extractor*
135 m
Volume available: 992 m3
Ventilation rate: 18 000 m3/h (1,4 ACH)
1,2 s
50,5 s after the release started
02 ≥ 18%
02 < 18%
During release:
After release:
*considering a trigger of the smoke extraction after 30 s
Acknowledgement : N.GAZIS (ESS)

## Slide 55: ODH case-study Accelerator tunnel
Chart: Oxygen concentration over time evolution (min)
| 0.0 | 0.0166 | 0.02166 | 0.1 | 0.3 | 0.4 | 0.52166 | 0.7 | 2.0 | 5.0
Oxygen concentration | 0.21 | 0.18394 | 0.17666 | 0.17671 | 0.17683 | 0.17689 | 0.17697 | 0.18034 | 0.19649 | 0.2078
ODH threshold | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Case 6: section between 2 exits – 2 smoke extractors*
135 m
Volume available: 992 m3
Ventilation rate: 18 000 m3/h (1,4 ACH)
1,2 s
40,9 s after the release started
02 ≥ 18%
02 < 18%
During release:
After release:
*considering a trigger of the smoke extraction after 30 s
Acknowledgement : N.GAZIS (ESS)

## Slide 56: ODH case-study Accelerator tunnel
Summary table
Case | Length of the tunnel | Ventilation system | Trigger time | Time needed to reach 18% O2
1 | 600 m | Normal | N/A | Always above 18%
2 | 135 m | Normal | N/A | 31,2 s
3 | 135 m | 1 smoke extractor | immediate | 22,3 s
4 | 135 m | 2 smoke extractors | immediate | 11,5 s
5 | 135 m | 1 smoke extractor | After 30 s | 50,5 s
6 | 135 m | 2 smoke extractors | After 30 s | 40,9 s
NOT REALISTIC

## Slide 57: ODH Safety process Preliminary ODH assessment
Method n°1 (CERN approach)
Objective: assess in a simple way consequences of the full loss of an asphyxiant fluid in a given volume without considering any ventilation and time parameter
Room parameters
Fluid parameters
O2 concentration
(perfect mixture)
+
Height of the gas layer
(stratification)
ODH Level
(O2≥18% OR O2<18%)

## Slide 58: ODH Safety process Preliminary ODH assessment
Method n°2 (Fermilab approach)
Objective: assess in a simple way the consequences of a leak of an asphyxiant fluid in a given volume considering the ventilation rate and the time evolution
Room parameters
Fluid + scenario characteristics
ODH parameters:
Fatality rate
Probability of fatality
ODH class
O2 evolution during fluid discharge
Part 1/2

## Slide 59: ODH Safety process Preliminary ODH assessment
Method n°2 (Fermilab approach)
Objective: assess in a simple way the consequences of a leak of an asphyxiant fluid in a given volume considering the ventilation rate and the time evolution
Contact persons
O2 evolution after fluid discharge
Part 2/2

## Slide 60: ODH control measures Which ones are relevant?
Simplication
of the approach to meet ESS needs…
OK
To be discussed
ES&H?
  “If this approach is taken, the ventilation system must now be treated as a safety system with appropriate controls and redundancies” – John Weisend, January 2015
PSS? IEC 61508?
Applicable?

## Slide 61: ODH control measures Other possible solutions…
Solution 1
Solution 2

## Slide 62: Practical cases Accelerator tunnel – Method n°1
Scenario: Helium discharge from the safety relief device of the insulating vacuum vessel from 1 High-β Cryomodule
Cause: leak from junctions/welds from the cavities
Volume of LHe: 1 x 4 x 0.048 m3
Temperature of LHe: 2K
Pressure: 1,9 bara
Tunnel: 12 600 m3 x 35% (full volume)
Volume of gas discharged: 174 m3
O2 concentration after discharge (homogeneous mixture): 20,17%
Height of gas layer (stratification): 0,05 m
ODH level: “SAFE”
Steady state
Acknowledgement : J.FYDRYCH (ESS)

## Slide 63: Practical cases Accelerator tunnel – Method n°1
Scenario: Helium discharge from the safety relief device of the insulating vacuum vessel from 1 High-β Cryomodule
Cause: leak from junctions/welds from the cavities
Volume of LHe: 1 x 4 x 0.048 m3
Temperature of LHe: 2K
Pressure: 1,9 bara
Tunnel: 4200 m3 x 35% (1/3 of the total volume)
Volume of gas discharged: 174 m3
O2 concentration after discharge (homogeneous mixture): 18,52%
Height of gas layer (stratification): 0,14 m
ODH level: “SAFE”
200 m
Acknowledgement : N.GAZIS, J.FYDRYCH (ESS)

## Slide 64: Practical cases Accelerator tunnel – Method n°2
Scenario: Helium discharge from the safety relief device of the insulating vacuum vessel from 1 High-β Cryomodule
Cause: leak from junctions/welds
Leak rate: 475 200 m3/h (ref. WP5_SafetySizing__nt-safety-devices-2015-01-14.docx)
Duration of the leak: infinite (not realistic)
Ventilation rate: 1 vol/h (12600 m3/h)
Tunnel: 12 600 m3 x 35% (full volume)
FORBIDDEN AREA
Control measures need to be taken
Steady state
Acknowledgement : J.FYDRYCH (ESS)

## Slide 65: Practical cases Accelerator tunnel – Method n°2
Scenario: Helium discharge from the safety relief device of the insulating vacuum vessel from 1 High-β Cryomodule
Cause: leak from junctions/welds
Leak rate: 475 200 m3/h (ref. WP5_SafetySizing__nt-safety-devices-2015-01-14.docx)
Duration of the leak: infinite (not realistic)
Ventilation rate: 1 vol/h (12600 m3/h)
Tunnel: 4200 m3 x 35% (1/3 of the total volume)
FORBIDDEN AREA
200 m
Control measures need to be taken
Acknowledgement : N.GAZIS, J.FYDRYCH (ESS)
Worst case scenario but maybe not realistic

## Slide 66: CERN LHC spill test Lessons learnt (from a Safety point of view)
The drop of O2 content cannot be related to the visible formation of mist in the flow
Exclusions zones have been increased
No personnel access to the tunnel while sectors are cooled down or warmed up or powering tests are performed of He cooled magnets
Access conditions for personnel redefined such that no exposure to a MCI larger than 0,1 kg/s
At kneeling height (0,5 m) O2 can drop to 11%
No safe zone available to put on the self-rescue mask
 | CERN LHC | ESS
Distance between rupture disks | 200 m | ?
Exclusion zones | Yes | Not applicable?
Acknowledgement : T.KOETTIG (CERN) – REFERENCE: Controlled cold helium spill test in the lhc tunnel at CERN