## Slide 1: Monolith Atmosphere Update
Leif Emås
15th TAC Meeting
April 6, 2017
www.europeanspallationsource.se

## Slide 2: Monolith Vessel & Nutron beam ports

## Slide 3: Monolith Vessel
Volume: 144 m3
Proton beam

## Slide 4: Monolith Vessel
Free volume: 41.8 m3
Proton beam
Inner shielding

## Slide 5: Four alternatives
Alternative 1: Helium atmosphere at 99.7 kPa
Alternative 2: High vacuum at 0.01 Pa
Alternative 3A: Rough vacuum at 10-100 Pa – air
Alternative 3B: Rough vacuum at 10-100 Pa – helium

## Slide 6: Alternativ 1: Helium atmosphere @ 99.7 kPa
Helium loop with purification and pressure control
Design loop flow 40 g/s (≈ 900 m3/h), He inventory ≈ 6.8 kg
Vacuum pumps for
rough vacuum

## Slide 7: Alternativ 2: High vacuum @ 0.01 Pa
Volume:
Atmosphere:
Pressure:
Weight air in vessel:
41.8 m3
Air + H2O
0.01 Pa
0.003 g
Cryochiller
TMP

## Slide 8: Alternativ 3A: Rough vacuum @ 10-100 Pa - air
Volume:
Atmosphere:
Pressure:
Weight air in vessel:
41.8 m3
Air
10-100 Pa
5-50 g
Multi-stage roots-rotor pump

## Slide 9: Alternativ 3B: Rough vacuum @ 10-100 Pa - He
Volume:
Atmosphere:
Pressure:
Weight He in vessel:
Weight He in loop:
41.8 m3
Helium
10-100 Pa
0.7-6.9 g
30 g
Multi-stage roots-rotor pump

## Slide 10: Requirements
NSS requirements with He @ 99,7 kPa are:
< 700 ppm N2 Partial pressure of < 70 Pa
< 30 ppm H2O Partial pressure of < 3 Pa
< 1000 ppm impurities partial pressure of < 100 Pa
Rationale:
Water and nitrogen under irradiation forms nitric acid which affects the super-mirror coating on the guides.

## Slide 11: Air removal capacity alt. 1 (He @ 99.7 kPa)
Chart: 
| 3.60000000000001E-5 | 0.0036 | 0.018 | 0.036 | 0.072 | 0.36 | 0.720000000000001 | 0.9 | 3.6 | 36.0 | 360.0 | 3600.0 | 36000.0
 | 0.00457 | 0.48 | 2.38 | 4.75 | 9.5 | 47.5 | 95 | 118.75 | 475 | 4750 | 47500 | 475000 | 4750000
 | 0.00143 | 0.1425 | 0.7125 | 1.425 | 2.85 | 14.25 | 28.5 | 35.625 | 142.5 | 1425 | 14250 | 142500 | 1425000
 | 0.00029 | 0.029 | 0.143 | 0.285 | 0.57 | 2.85 | 5.7 | 7.125 | 28.5 | 285 | 2850 | 28500 | 285000
 | 3.6e-05 | 0.00356 | 0.0178 | 0.0356 | 0.0712 | 0.356 | 0.712 | 0.8906 | 3.562 | 35.635 | 365.25 | 3562.5 | 35625
Removal efficiency: 97%
Air leakage (g/h)
Purification flow
0.3 g/s
1 g/s
5 g/s
40 g/s
Air content at steady state = f (air leakage)
Air content in He (ppmV)
Permissable air content in helium atmosphere (870 ppmV)
882 g/h

## Slide 12: Water removal capacity alt. 1 (He @ 99.7 kPa)
Chart: 
| 0.0036 | 0.36 | 0.630000000000001 | 1.8 | 3.6 | 7.2 | 10.8 | 12.6 | 36.0 | 108.0
 | 0.229 | 22.927 | 40.12 | 114.6 | 229 | 458 | 688 | 802 | 2293 | 6878
 | 0.7642 | 76.42 | 133.76 | 382.11 | 764.22 | 1528 | 2293 | 2675 | 7642 | 22926
 | 0.046 | 4.585 | 8.024 | 22.93 | 45.85 | 91.7 | 137 | 160 | 458 | 1375.6
 | 0.0057 | 0.57 | 1 | 2.9 | 5.7 | 11.5 | 17.2 | 20.06 | 57.32 | 172
Removal efficiency: 97%
Water leakage (g/h)
Purification flow
0.3 g/s
1 g/s
5 g/s
40 g/s
Water content at steady state = f (water leakage)
Water content in He (ppmV)
Permissable water content in helium atmosphere (30 ppmV)
18.8 g/h

## Slide 13: Argon accumulation alt. 1 (He @ 99.7 kPa)
Air leakage
0.5 g/h
1 g/h
2 g/h
5 g/h
10 g/h
Operating time (hours)
Argon partial pressure = f (operating time)
Argon partial pressure (Pa)
Chart: 
| 0.0 | 1000.0 | 2000.0 | 3000.0 | 4000.0 | 5000.0
 | 0 | 9.4798 | 18.9596 | 28.4394 | 37.9192 | 47.399
 | 0 | 18.9596 | 37.9192 | 56.8788 | 75.8384 | 94.798
 | 0 | 37.9192 | 75.8384 | 113.7576 | 151.6768 | 189.5959
 | 0 | 94.798 | 189.5959 | 284.3939 | 379.1919 | 473.9898
 | 0 | 189.5959 | 379.1919 | 568.7878 | 758.3838 | 947.9797
Renew helium (6.8 kg)
Annual helium consumption approx. 14 kg with an air leakage of 2 g/h
10 g/h
0.5 g/h
1 g/h
2 g/h
5 g/h

## Slide 14: Air removal capacity alt. 2 (0.01 Pa)
0.01 Pa
Turbo molecular vacuum pump
Pumping speed:
Pumping speed:
48 m3/min
3.5 mg/min
Atmosphere:
Pressure:
100% air
0.01 Pa
Air partial pressure (Pa)
Pumping speed (l/s)

## Slide 15: Water removal capacity alt. 2 (0.01 Pa)
0.01 Pa
Polycold MaxCool 2500 L Cryochiller
Pumping speed:
Pumping speed:
8,400 m3/min
1.0 g/min
Atmosphere:
Pressure:
100% water
0.01 Pa
Water vapor partial pressure (Torr)
Pumping speed (l/s)

## Slide 16: Air removal capacity alt. 3A (air @ 90 Pa)
90 Pa
Multi-stage roots-rotor vacuum pump
Pumping speed:
Pumping speed:
5 m3/min
3.3 g/min
Atmosphere:
Pressure:
100% air
90 Pa (N2 partial pressure 70 Pa)
Pressure (Pa)
Pumping speed (l/min)

## Slide 17: Water removal capacity alt 3A (water @ 3 Pa)
3 Pa
Multi-stage roots-rotor vacuum pump
Pumping speed:
Pumping speed:
4 m3/min
0.14 g/min
Atmosphere:
Pressure:
100% water
3 Pa
Pressure (Pa)
Pumping speed (l/min)

## Slide 18: Air + H2O removal capacity alt. 3B (He @ 100 Pa)
100 Pa
Multi-stage roots-rotor vacuum pump
Atmosphere:
Pumping speed:
Pumping speed:
87% air + 10 % He + 3% H2O
3.2 g/min of air
0.18 g/min of H2O
Atmosphere:
Total pressure:
Pumping speed:
He + air + H2O
100 Pa
5 m3/min
Pressure (Pa)
Pumping speed (l/min)

## Slide 19: Argon accumulation alt. 3B (He @ 10-100 Pa)
Chart: 
| 0.0 | 1000.0 | 2000.0 | 3000.0 | 4000.0 | 5000.0
 | 0 | 189.5959 | 379.1919 | 568.7878 | 758.3838 | 947.9797
 | 0 | 947.9797 | 1895.9594 | 2843.9391 | 3791.9188 | 4739.8985
 | 0 | 1895.9594 | 3791.9188 | 5687.8782 | 7583.8375 | 9479.7969
Air leakage
10 g/h
50 g/h
100 g/h
Operating time (hours)
Argon partial pressure = f (operating time)
Argon partial pressure (Pa)
Renew helium (1,5 + 30 g)
Annual helium consumption approx . 2.25 kg with an air leakage of 50 g/h
100 g/h
50 g/h
10 g/h

## Slide 20: Maximum allowed air and water leakage
Alternative 1 | g/min | g/hour | kg/24 hours | kg/5000 hours
Air | 14.7 | 882 | 21.2 | 4,410
Air due to Ar build-up | 0.03 | 2 | 0.048 | 10
Water | 0.31 | 18.8 | 0.45 | 94
Alternative 2 | g/min | g/hour | kg/24 hours | kg/5000 hours
Air | 0.0035 | 0.21 | 5.04 | 1.05
Air due to Ar build-up | Non-limiting |  |  | 
Water | 1.0 | 60 | 1.44 | 300
Helium atmosphere @ 99,7 kPa
High vacuum @ 0.01 Pa

## Slide 21: Maximum allowed air and water leakage
Alternative 3A | g/min | g/hour | kg/24 hours | kg/5000 hours
Air | 3.3 | 198 | 4.75 | 990
Air due to Ar build-up | Non-limiting |  |  | 
Water | 0.14 | 8.4 | 0.20 | 42
Alternative 3B | g/min | g/hour | kg/24 hours | kg/5000 hours
Air | 3,2 | 192 | 4.61 | 960
Air due to Ar build-up | 0.83 | 50 | 1.2 | 250
Water | 0.18 | 10.8 | 0.26 | 54
Rough vacuum @ 10-100 Pa - air
Rough vacuum @ 10-100 Pa - He

## Slide 22: Result
 | Alt 1 | Alt 2 | Alt 3A# | Alt 3B
Air removal capacity (g/h) | 2 | 0.21 | 198 | 50
Water removal capacity (g/h) | 18.8 | 60 | 8.4 | 10.8
Helium atmosphere @ 99,7 kPa
High vacuum @ 0.01 Pa
Rough vacuum @ 10-100 Pa - air
Rough vacuum @ 10-100 Pa - He
# Pumping capacity can easily be increased by installing more pump(s)

## Slide 23: Result
 | Alt 1 | Alt 2 | Alt 3A# | Alt 3B
Air removal capacity (g/h) | 2 | 0.21 | 198 | 50
Water removal capacity (g/h) | 18.8 | 60 | 8.4 | 10.8
Remove PBW | No | Yes | No | No
High vacuum standards | No | Yes | No | No
Helium consumption | High | None | None | Low
Heat removal (from nutron beam guides) | Good | Enough? | Enough? | OK
System simplicity | - | + | ++++ | ++
Helium atmosphere @ 99,7 kPa
High vacuum @ 0.01 Pa
Rough vacuum @ 10-100 Pa - air
Rough vacuum @ 10-100 Pa - He
# Pumping capacity can easily be increased by installing more pump(s)

## Slide 24: Conclusion
Decision
Alternative 3: Rough vacuum 10-100 Pa with PBW
It is not decided if the rough vacuum shall consist of air (air + water) or helium (He + air + water).

## Slide 25: Pros & cons for alttenative 3A and 3B
Cons
Proton Beam Window required
Pros
Very/fairly simple and reliable system (air/helium)
Does not require high vacuum standards
None/low helium consumption (air/helium)
Viscous (laminar) flow region – high pumping capacity
Pumping capacity can easily be increased (air)
Quick pump down time to rough vacuum (3,25 hours)

## Slide 26: Thank you.
www.europeanspallationsource.se
April 6, 2017