## Slide 1: ACCSYS WP16 Cooling Support
Anton Lundmark
Cooling System Engineer
www.europeanspallationsource.se
17 March 2017

## Slide 2: WP16
Anton Lundmark – WP leader
Akif Coku – Lead Engineer
Fredrik Persson – Piping design Engineer
Additional designer – TBD
2 x Technicians TBD
Support from other groups:
  Ola Ingemansson (Target) – Instrumentation
  Emil Lundh (EIS) – Computational Fluid Dynamic
  Anders Olsson (EIS) – Structural analyses
  Leif Emås (Target) – Process design
  Martin Hansson (CF) – Process design and interfaces with CF

## Slide 3: Process groups at ESS
NSS design teams
Target Fluid Systems group
Accelerator design teams
WP 16
Requirements coordination
Interface to AD & NSS
Secondary systems
CF Process
Central processing plant
Site distribution + main headers in buildings
CF HVAC
Heating
Cooling
District Heating

## Slide 4: CF Process - design parameters

## Slide 5: ESS site layout
Accelerator tunnel – G01
RF gallery – G02
Accelerator tunnel
Test stands – G02
Central processing plant
Compressor building – G04

## Slide 6: WP16 interfaces to Accelerator/Conventional facilities
CF Process Systems
ACC Tunnel (G01):
IS
LEBT MEBT
RF couplers (SPK, MBL, HBL)
WP16
Cooling
RF Gallery (G02):
Modulators
Klystrons/Tetrodes
Circulators/Loads
Power supplies
Test Stands (G02):
Modulators
Klystrons
Circulators/Loads
RF couplers
Cryogenics (G04):
Oil coolers
Gas coolers
Turbine brakes
Electrical motors

## Slide 7: Overview – tunnel cooling
RFQ cooling skid - WP 3
DTL cooling skid - WP 3
IS/LEBT/MEBT cooling skid – WP16
  85 kW, 14.5 m3/h
RF Coupler/Magnet Cooling skid – WP16
  500 kW, 85 m3/h

## Slide 8: Overview - tunnel cooling

## Slide 9: Status of tunnel cooling systems
Interface requirements for accelerator components defined
Statement of works written for tunnel distribution piping (combined with cable trays) and WP16 skids
Procurements to be launched any day
  Slightly later than planned due to detail design issues such as RFQ valve location discussions, pipe routing issues, input from CF, as well as procurement group prioritizations
  WP16 will provide detailed piping design for tunnel
Ongoing tasks are:
  Coordination of rules for penetrations through fire walls and radiation shielding – CF / AD safety group
  Development of piping specifications (for piping design tool) together with Integration & Engineering support group
  3D model review - integration work in order to avoid clashes
  Writing report on water activation
  Coordination together with target design teams in order to harmonize tools and design solutions, hook-ups, supports, instruments
  Coordinating procurement together with WP15 (electrical support)
  Drafting WSCP (working safety coordination plan)
  Fluid dynamics analysis of magnet coupler branch (see separate slide)

## Slide 10: Ongoing work
Fluid analysis in Dymola of coupler/magnet circuit

## Slide 11: Cooling for Test stand 2
Detail design ongoing
  Piping design depends on RFDS support design
  Envelopes for manifolds, skids, etc. defined together with Test Stand group
Working with RF group to define instrumentation
  Will launch tender as soon as possible
Separate skid for cryomodule RF couplers
  Solves low design pressure issue (max 3 bar(g) for couplers)
  No risk of contaminating CF main system

## Slide 12: Cooling for RF gallery
Basic design in place
  P&ID:s ready
  Envelopes defined
  Piping loads onto RFDS support structure defined
  Interfaces with CF defined (including concept for heat recovery)
  Interfaces with RF group defined
  Interfaces with racks defined
No information on RFDS supports structure for DTL and RFQ area
Ongoing design of RFDS supports structures for Spoke, MBL, and HBL
Notes: Heat recovery

## Slide 13: G02 RF gallery (DTL/RFQ area)

## Slide 14: G02 RF gallery (MBL/HBL area)

## Slide 15: G04 (compressor building for CRYO) water cooling
Dedicated cooling water circuit for cryoplant (quality constraints of available cooling water in the building)
Subsystem design and commissioning is CF scope.
Compr. motor
Middle temperature Return
Middle temperature Supply
Oil vessel
Helium compressor
Helium cooler
Oil
cooler
He to fine oil removal
He from cold box
High temperature Return
Middle temperature Return
27°C
27°C
30°C
30°C
30°C
39°C
71°C
39°C
83°C
49°C
74°C
40°C
69°C
37°C

## Slide 16: Schedule
Start of piping installation
FEB level 100 access
“LOT 2” of tunnel piping – small bore piping/manifolds

## Slide 17: Schedule
Installation of first skid
Installation of cooling system for RF

## Slide 18: Cooling for NSS
WP16 scope:
  Complete design and installation for NMX
  Cooling skids and piping for bunker
  Detailed piping design + manufacturing of cooling skids for LOKI and FREIA
  Detailed piping design and skid specifications for other instruments
  Limited “material” scope but lot of design work and coordination
Ongoing tasks:
  Bunker design – coordination of piping penetrations and routing of piping inside bunker
  Drafting interface requirements

## Slide 19: LoKI
Type of instrument: SANS
Typical components requiring cooling: HVAC units, Choppers, Racks

## Slide 20: Summary and plan forward
Initiate and oversee installation of tunnel piping
Launch and manage procurement of 2 cooling skids
Launch installation of TS2 cooling system (cryomodule cooling later stage)
Plan tunnel installation LOT 2, i.e. detail design of small bore piping for magnets, couplers, manifolds
Plan installation of DTL/RFQ RF gallery area
Define requirements with NSS