## Slide 1: Micro TCA.4, Motion control Hardware and software support for WS WS PDR-2
Daniel Piso Fernández
Hardware and Integration Group Leader
www.europeanspallationsource.se
2016-12-13

## Slide 2
ESS ERIC BOARD OF DIRECTORS DIRECTOR GENERAL
MACHINES DIRECTORATE
SCIENCE DIRECTORATE
ACCELERATOR
TARGET
PROJECT SUPPORT & ADMINISTRATION DIRECTORATE
Communication
Operations, ES &H and QA
CONVENTIONAL FACILITIES
HUMAN RESOURCES
GENERAL SERVICES
SCIENTIFIC PROJECTS
SCIENTIFIC ACTIVITIES
NEUTRON TECHNOLOGIES
NEUTRON INSTRUMENTS
INTEGRATED CONTROL SYSTEM
SYSTEMS ENGINEERING
DATA MANAGEMENT SOFTWARE CENTRE
ENGINEERING & INTEGRATION SUPPORT
COMMUNICATIONS & EXTERNAL RELATIONS
FINANCE
INFORMATION TECHNOLOGY
LEGAL
SUPPLY, PROCUREMENT & LOGISTICS

## Slide 3: What is ICS about?
The ESS facility is a large and complex machine with very, very much equipment that needs to work in synchronization - and with well-known configurations
  Power Supplies
  Vacuum systems
  Cryogenic System
  Water Cooling Systems
  RF equipment
  Beam Instrumentation
  Building Management Systems
For this purpose almost all equipment at the ESS facility is connected to the Integrated Control System.
The goal is to create an abstraction of the whole machine in Process Variables that allows the operation of the machine as a whole
An estimated 1.5 million Process Variables will be needed

## Slide 4: Top Level Requirements
Provide the following to ESS:
  Control system framework for monitoring and control of accelerator, target, instruments and conventional facilities (EPICS)
  Timing service for generating events, synchronization of devices and time stamping (in the ns range)
  Control system services and applications to perform commissioning and operations
  IOC and Integration Support to stakeholders
  Machine Protection and Personnel Safety systems
  Control Room(s)
Constraining requirements
  High reliability and availability!

## Slide 5: Technology scope for ICS
The span of technical scope and the competencies needed in ICS is enormous
The processes and the different stages in the lifecycle have to be adapted to the development of different technologies (e. g. Agile development for Sofware vs. Classical development cycles for hardware).
Electronics hardware
Software
PLC
Infrastructure
Analog electronics
Digital electronics
FPGA firmware
Digital communication
PCB, packaging
Test and validation
Industrialization, maintenance
Kernel drivers
Operating systems (RT)
Development environments
EPICS
CSS/Eclipse
Applicatoins (GUI, Web, Services)
Databases
Availability, performance
Test and validation
Safety and protection

## Slide 6: ICS Organization 2016-11-07
Henrik Carling
Division head
Anna Gillberg
Team assistant
Annika Nordt Safety and protection
Daniel Piso
Hardware and integration
Hector Novella
Deputy project manager
Susanne Regnell
Control Software
Timo Korhonen Chief engineer
Emanuele Laface
Accelerator physicist
Juan Esteban Müller
Software scientist
Leandro Fernandez Senior software engineer
Ricardo Fernandes Senior software engineer
Claudio Rosati
Software engineer
Javier Cerejo PhD Student
Angel Monera
FPGA Engineer
Denis Paulic
PLC Engineer
Manuel Zaera-Sanz
PLC Engineer
Morteza Mansouri
Safety Engineer
Riccard Andersson PhD student
Stuart Birch Senior safety engineer
Ben Folsom
PhD student
Remy Mudingay Infrastructure engineer
Temporary employee
Employee
Consultant
Consultant off-site
Joao Martins
Integrator
Benedetto Gallese
Integrator
Yong Kian Sin IEC61508 engineer
François Bellorini
Integrator
David Brodrick
Integrator
IT/Infrastructure
Position under consideration
Alexander Söderqvist
Integrator
Jeong Han Lee Integrator
Consultants
Julen Etxeberria
Intern
Open positions (2)
Open positions (2)
Open positions (2)
Simone Farina Embedded systems egineer
Szandra Kövecses
Technical coordinator
Niklas Claesson
Integrator
Krisztián Löki
Integrator
Thilo Friedrich
PhD student
Nick Levchenko
Integrator
Alessio Curri ICS administrator
Karin Rathsman Senior scientist
Start 2017-02-01
Start TBD
Start 2017-02-01
Viktor Fred
Electrical engineer
Fredrik Luthander
Software engineer
Wojtek Fabianowski in-kind manager
Jan-Åke Persson
Senior software engineer
Start TBD
Benjamin Bertrand
Software engineer
Start 2017-02-01
End 2016-12-31

## Slide 7: ESS In-kind Goals
Chart: 
| Controls | Target | Instruments (NSS) | Accelerator
IKC | 36.5 | 101 | 228 | 382
Cash | 36.5 | 54 | 122 | 128
€ 510 M
€ 350 M
€ 155 M
€ 73 M
Construction cost: € 1.84 Billion (2013 €)
In-kind: € 747.5 Million
M€
ICS

## Slide 8: ICS In-kind partners
Agreement signed
Agreement waiting for signature
Early discussions
Collaboration agreement
Partner Institutes
Atomki, Hungary
CEA, France
CNRS/IPNO, France
Elettra, Italy
ESS Bilbao, Spain
IFE, Norway
INFN Catania, Italy
INFN Legnaro, Italy
PSI, Switzerland
Tallinn Technical University, Estonia
ÚJV Řež, Czech Republic
University of Łódź , Poland
Uppsala University, Sweden
ZHAW, Switzerland

## Slide 9: ICS - construction phase value envelope
The ICS value envelope for the construction phase shows the aggressive project schedule
A majority of the ICS value is labor based effort (i.e. not equipment)
The ICS estimated headcount envelope reveals large in-kind/supplier opportunities

## Slide 10: ICS in-kind portfolio development
Wojtek Fabianowski has started taking responsibility for driving in-kind activities at ICS
Since last IKRC one in-kind schedule (Technical Annex ) has been signed with ESS Bilbao for MEBT Controls at (863 k€)
Most other in-kind projects are running more or less according to plan
Situation in Switzerland is particularly problematic due to cash-flow (!) issues

## Slide 11: Control System Integration
(ISO/IEC/IEEE 15288) describes integration in a system life cycle process perspective as “to synthesize a set of system elements into a realized system (product or service) that satisfies system requirements, architecture and design”
The scope of the Integration Team is to perform of the development of control systems from requirements engineering, design, implementation, procurement and delivery for installation, verification and support by using the components provided by other teams.
Goals
  Achieve a proper abstraction of subsystems/devices as a collection of EPICS PVs, to permit operation and monitoring
  Remote access to all local control parameters and all data that is potentially relevant/interesting for operation and maintenance.
  Data in a form that allows correlation across the machine
Approach
  The machine is huge – design for uniformity
  Interface to similar local control is uniform
    DAQ boards, Power supplies, motion control, imaging, …
  Provide subsystems/devices data in a standard form
  Keep the amount of different types of hardware to support as low as possible
  Use common software components whenever possible
  Focus on documentation on support to developers and integrators

## Slide 12: Standardization
Crucial for controls
Affects costs and even the shape of the teams on the short term and operation costs in the long term
It is important to understand standardization as lifecycle management

## Slide 13: Distributed Life Cycle
ICS Handbook
Machine Protection Requirements
ICS Integration strategy
ICS Standard for Electrical Equipment

## Slide 14: Organizational setup – Task Allocation
The team, as the rest of ICS is organize in a classical matrix structure
It provides resources to 6 workpackages representing about 40% of the project value
The matrix allows flexibility in assigning resources and managing prioritization
At least in theory, everyone is available for any task!
The long term goal is to set up metrics (KPIs) to measure and improve the efficiency of the team and the processes related to integration

## Slide 15: Distributed development
15
ESS EPICS Environment

## Slide 16: Hardware Strategy. Threefold structure for generic I/O
  Fast real-time processing, FPGAs
    MTCA.4
    Use only where needed (high cost, specialization)
    Extensively use FMC (Vita-57) mezzanine cards
  Real-time industrial-type I/O
    EtherCAT, on IOC
    Low cost, distributed, good real-time performance
    Moderate speed (e.g. up to 100 kSPS A/D conversion)
  Process I/O with no tight synchronization requirements
    PLCs (Siemens)
  In addition, prepare integration of off-the-shelf devices
    Serial and LAN interfaces

## Slide 17: µTCA Infrastructure: crates
Plans to support two crate variants :
12 slots 9U for systems requiring more than 6 AMCs and/or more than 4 RTMs;
Constraints:
Cooling scheme: front to rear, defined by rack ventilation;
Triggers and Interlocks: signals conveyed to all AMCs, M-LVDS lines availability;
ISSUE: very few options for 3U crates with front to rear cooling
6 slots 3U to reduce the number of racks deployed.

## Slide 18: µTCA Infrastructure: MCH & PM
MicroTCA Carrier Hub :
N.A.T. selected, less interoperability issues found up to now.
Power Modules:
Many products under review:
Telkoor
Wiener
N.A.T.
Final choice made according to instrument requirements and space constraints.
More than one product might be selected.

## Slide 19: Hardware Strategy. I/O Controller variants
  MTCA.4 based digital front-end platform
    MTCA.4 AMC with a FPGA, CPU and modular interfaces
      Two variants (IFC1410, IFC1420)
      Back-up solutions: Typical mTCA configuration with Struck or FMC carrier.
    In-kind contribution from Switzerland
      PSI and the company IOxOS SA
  Industrial PCs where appropriate
  Virtualized IOCs running on server infrastructure
    No tight real-time requirements or pulse-to-pulse data
    Site infrastructure systems, cryogenics, vacuum, cameras
    Redundant fail-over clusters
    Typically interfacing PLC-based systems, cameras
  possible mini-IOC
    Concept study ongoing
    Integrated timing and processing unit

## Slide 20: AMC boards: ICS supported
Beam Instrumentation built using 2 AMC boards provided by PSI through In-Kind
IFC1410:
Support for 2 HPC FMC cards
PPC and Kintex Ultrascale FPGA
Zone 3 assignment according to DESY recommendation for digital applications
IFC1420:
Similar digital architecture to IFC1410
Upper FMC slot replaced by mezzanine card with ADCs
Zone 3 assignment according to DESY Class A1 recommendation for analog applications

## Slide 21: Back-up solution (LLRF; BPM;BCM)
10 Channels 125 MS/s 16-bit ADC
10 MS/s to 125 MS/s Per Channel Sampling Speed
AC or DC Input Stage
Internal, Front Panel, RTM and Backplane Clock Sources
Two 16-bit 250 MS/s DACs for Fast Feedback Implementation

## Slide 22: FMC cards: ICS supported
ACQ420 (4 channel 16-bit 500 to 2000 ksps)
AD/DA Converter boards:
DAC 3113 (dual channel 16-bit/500 Msps DAC and 2 channels 16-bit/250 Msps ADC
FM-S14 (Quad-SFP/SFP+ up to 10Gbps)
FMC-4SFP+ (Quad/Dual-SFP/SFP+)
Additional FMC cards might be supported according to BI requirements
ADC 3112 (4 channels 12-bit/900(1000) Msps
or 2 channels 12-bit/1800(2000) Msps)
ADC 3110/3111 (8 channel 16-bit 250Msps)
High speed interface cards:
EtherCAT slave, in-kind project (Estonia)

## Slide 23: Motion Control

## Slide 24: Motion Control – Useful Information
Useful Links:
Open source Motion control
  https://ess-ics.atlassian.net/wiki/display/MCAG/Open+Source+Motion+Control
  https://bitbucket.org/europeanspallationsource/ecmctraining
Scanning Application
  https://ess-ics.atlassian.net/wiki/display/HAR/Scanning
PSI:
  https://ess-ics.atlassian.net/wiki/display/HAR/EtherCAT

## Slide 25: Timing System Status
All components selected
  Receivers tested and in operation
  Went up a learning curve (Catania setup, etc.)
  Work is starting with the event master setup in lab
    Build a realistic model of the full distribution, with events and data
Long haul cabling planned
  Thanks to Remy Mudingay!
    synergy with network cabling
  Deployment details to be worked out
User guides have been produced
  MTCA and PCI EVRs
  Jeong Han Lee & Javier Cereijo Garcia
Extending functionality (in EPICS)
  MTCA specifics: backplane clocks, triggers

## Slide 26: System layout principle
EVG
EVR
EVR
EVR
EVR
EVR
EVR
Actual location of EVG to be defined, should be next to RF Master Oscillator
Long-haul fan-outs single mode optical fiber, short haul to EVRs multimode (OM4)
fan-out
fan-out
fan-out
fan-out

## Slide 27: Some performance numbers
RF input frequencies 50 MHz to 1.6 GHz
  Frame frequency derived from this (~2 to ~143 MHz, maybe more)
  Frame frequency defines the base time resolution
EVR synchronization to RF (aka jitter) in order of a few ps RMS
Time resolution 1/(frame frequency)
  ESS case: 1/88.0525 MHz , about 11 ns
  Special outputs (CML) achieve 1/40 of that (280 ps @ ESS)
  With high-resolution output modules, 10 ps steps available
64-bit timestamps (32 bit seconds, 32-bit “tick” counter)
  Latched on event reception (backtrack to real HW time)
Active (propagation) delay compensation
  To counter e.g., thermal drifts due to fiber expansion

## Slide 28: Event generator and fanout (EVM)
EVM – Event Master
(Event Generator and Fanout)
Fanout in ICS lab
(poor photo quality)
Fanouts will be run as standalone units in 1U
“pizza”boxes. Only network connection is needed.

## Slide 29: Event Receivers
MTCA.4
PCIe (for industrial PCs, etc.)

## Slide 30
?