## Sheet1
| Failure rate estimations for the accelerator cryogenic buildings (G02, G04 and CTL Gallery) | [5 empty] | Prepared by: Duy Phan, Xiaotao Su Reviewed by: Philipp Arnold Approved by: Philipp Arnold ESS-0126762
Building | Room | Item | Number of items | Total length (m) | Type of failure | Failure rate per item (event/hour or event/meter-hour) | Total failure rate (event/hour)
G04 | ACCP Hall (ACH) | Flanges | 23 |  | Rupture | 1e-09 | 2.3e-08
|  | Safety relief devices | 8 |  | Rupture | 5e-10 | 4e-09
|  | Valves | 229 |  | Rupture | 5e-10 | 1.145e-07
|  | Piping |  | 535 | Rupture | 3e-11 | 1.605e-08
[6 empty] | TOTAL ACH | 1.5755e-07
| TMCP Hall (TCH) | Flanges | 48 |  | Rupture | 1e-09 | 4.8e-08
|  | Safety relief devices | 20 |  | Rupture | 5e-10 | 1e-08
|  | Valves | 173 |  | Rupture | 5e-10 | 8.65e-08
|  | Piping |  | 1377 | Rupture | 3e-11 | 4.131e-08
[6 empty] | TOTAL TCH | 1.8581e-07
| HP Gas Storage (HPGS) | Flanges | 2 |  | Rupture | 1e-09 | 2e-09
|  | Safety relief devices | 20 |  | Rupture | 5e-10 | 1e-08
|  | Valves | 19 |  | Rupture | 5e-10 | 9.5e-09
|  | Piping |  | 30 | Rupture | 3e-11 | 9e-10
[6 empty] | TOTAL HPGS | 2.24e-08
[6 empty] | TOTAL G04 | 3.6576e-07
Building | Room | Item | Number of items | Total length (m) | Type of failure | Failure rate per item (event/hour or event/meter-hour) | Total failure rate (event/hour)
G02/G01 | Cryogenic Transfer Line Gallery (CTLG) | Flanges |  |  |  |  | 0
|  | Safety relief devices |  |  |  |  | 0
|  | Valves |  |  |  |  | 0
|  | Piping |  | 3553 | Rupture | 3e-11 | 1.0659e-07
[6 empty] | TOTAL G02 | 1.0659e-07
Building | Room | Item | Number of items | Total length (m) | Type of failure | Failure rate per item (event/hour or event/meter-hour) | Total failure rate (event/hour)
G02 | Coldbox Hall (CXH) | Flanges | 53 |  | Rupture | 1e-09 | 5.3e-08
|  | Safety relief devices | 98 |  | Rupture | 5e-10 | 4.9e-08
|  | Valves | 479 |  | Rupture | 5e-10 | 2.395e-07
|  | Piping |  | 2141 | Rupture | 3e-11 | 6.423e-08
[6 empty] | TOTAL G02 | 4.0573e-07
References:
1: - Safety devices list for ODH assessment, X.Su
- Valve list for ODH assessment, X.Su
- Flange list for ODH assessment, X.Su
2: - Interconnecting pipe list, X.Su
3: - FESHM 4240: Oxygen Deficiency Hazards (ODH), Fermilab
1
2
3
2
1
2
3
2
1
2
3