## Slide 1: Bunker Wall Design Wall 2018-01-31
Thorbjörn Lindwall
Design engineer
www.europeanspallationsource.se
26 January, 2018

## Slide 2
Content
1. Wall Layout
Wall Names
2. Curved Walls (R15 & R28)
Layers
Wall Blocks
Utility Feedthrough
3. Mid Walls
Layers
5. Temporary Shielding
Wall Blocks
6. Corner Blocks
Walls Blocks
Piping

## Slide 3
Wall Top Assm
ESS-0053441
Wall Assm - West
Wall Assm - South- Reduced
Wall Assm - North
Wall Assm – East - RS
Mid Wall East
Mid Wall West
Wall Names
Bunker walls Top View

## Slide 4
Curved Walls (R15 & R28)
Wall Layers
The bunker walls are made up from
50mm layers of HDPE and Steel.
Each 6° wall sections contains 17
Wall blocks.
From inside to outside:
450mm HDPE Borated
150mm Steel
150mm HDPE
300mm Steel
150mm HDPE
200mm Steel
150mm HDPE
200mm Steel
300mm HDPE
150mm Steel
300mm HDPE
150mm Steel
250mm HDPE
150mm Steel
300mm HDPE Borated
HDPE shown in red.
Steel shown in grey.
Inside Outside
Complete R28 wall section

## Slide 5
Curved Walls (R15 & R28)
Wall Blocks
Pictures shows a typical design
of wall blocks.
The steel and HDPE layers in each block
are hold together using 50 or 60mm steel
Rods. The rods are welded in the outer
layers of the blocks.
For the block facing inside of the bunker we can’t have
steel bolts thru the first block of HDPE.
These layers of HDPE will be welded or screwed (HDPE screws)
together to a 450mm thick block.
On the first steel layer a side plate will be welded.
The HDPE block will then be screw from the side to the block
using screws for plastic/wood .
Side plate

## Slide 6
Curved Walls (R15 & R28)
Utility feedthrough
Pictures shows a typical design
of wall blocks.
To provide instrument technology inside the
bunker each wall section has a utility feedthrough integrated in the top wall blocks.
For R28 wall sections the feedthrough is 1000x300mm.
For R15 wall sections the feedthrough is
700x300mm.
The feedthrough have 300mm chicane to prevent radiation leak.
To increase the access to the feedthrough a removable block on the outside is added. This block also works as the end block of the chicane.
The utility block is hold in place with two pins.

## Slide 7
Mid Walls
Mid Walls
Same thickness and layout as for the roof.
From inside to outside:
100mm HDPE Borated
50mm Steel
200mm HDPE
450mm Steel
400mm HDPE
250mm Steel
100mm HDPE Borated
Inside
Outside
HDPE shown in red.
Steel shown in grey.

## Slide 8
Temporary Shielding
Wall Blocks
Pictures shows a typical design
of wall blocks.
To reduce the cost for the bunker we can use
temporary shielding in some areas. These
blocks are made of heavy concrete.
Temporary shielding
Temporary shielding
R15 temporary shielding
Assembly contains five
unique blocks. Block
weight up to 11600Kg.
R28 temporary shielding
Assembly contains three
unique blocks. Block weight
up to 14000Kg.

## Slide 9
Wall Blocks
The corner blocks are used as end pieces
for the R28 walls. They are the interface
between CF building and bunker wall.
Material is heavy concrete.
Piping
One of the mid block contains a feedthrough
for cooling pipes. The pipes are used for
cooling instrument technology inside the
bunker. All of the pipes will be casted in
to the block wall block. This is to reduce
radiation leak as much as possible.
The pipes are also bent to create a internal chicane
in the block. The design of these pipes are not
yet compete.
Pictures show a concept design of the wall blocks.
Mid block with pipes Top view
Corner Blocks
Corner blocks
Corner blocks
(Not latest design)
Mid block with pipes Side view
Complete corner block assembly

## Slide 10
On the 22nd of January a decision was made to
replace the laminated bunker walls with heavy concrete walls.
This means that we are back on square one and will start over with the design of the walls.