## DOORS Req. format
Requirement attributes. Help can be obtained by hovering with the mouse over any of the titles of the columns | [18 empty] | These are not requirement attributes and will not be imported into DOORS
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Comments
Ducting
|  | Ducting System - Life time of ducting system | H09 Electrical ducting system shall be designed for a life time to at least 2065. |  | SW | Design Manual, ESS-0007857
|  | Ducting System - Separated ducting systems | H09 Electrical ducting system shall be separated in at least three parts; power cables, communication cables and cables for fire safety systems. |  | SW | Design Manual, ESS-0007857
|  | Ducting System - Dimensioning of ducting system | H09 Electrical ducting system shall be sized to cover cable installations related to CF. |  | SW | Design Manual, ESS-0007857 | [13 empty] | ELECTRICAL DUCTING GROUND is found in ESS-0206993 ELECTRICAL DUCTING PLAN is found in ESS-0206995
Power demand
|  | LV Power Supply - Metering of lighting loads. | H09 Electrical panel board shall have a meter for lighting circuits, to allow for energy consumption for lighting installations to be metered. |  | SW | BREEAM
|  | LV Power Supply - source | H09 shall be supplied with power from D05 substation, both grid power and back-up power |  |  | ESS-0083112 4.10
|  | LV Power Supply - source | Systems critical to the process shall be connected to backup power |  |  | ESS-0083112 4.11
|  | LV Power Supply - source | Critical functions related to shielding and radiation protection of the staff, contamination control, confinement, containment and environmental monitoring shall automatically be connected to backup power and prepared to be connected to UPS-power. (UPS not in CF scope) |  |  | ESS-0083112 4.11
|  | LV Power Supply - Loads | H09 Power supply is dimensioned to fulfill requirements in ICD |  |  | ESS-0145269
|  | HV- and LV system power measurements | It shall be possible to perform continuous energy measurement on symmetric and asymmetric loads both on the HV- and LV systems. Error tolerance = 1,0% (MID Class B) | EHS-NRG-011 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [12 empty] | SRH09-11
|  | Lighting power measurements | It shall be possible to measure electrical consumption of Lighting only, separated from all other electricity consumption | EHS-NRG-013 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [12 empty] | SRH09-13
|  | Electrical installations | Electrical installations shall comply to SS-EN-ISO | EHS-FIR-001 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-66
|  | Cable installations | Cables shall be fire retardant and non corrosive in compliance with ESS-0034035 | EHS-FIR-011 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-67
|  | Insulation and grounding | Switches and breakers shall be installed and easily identified for quick and remote insulation and grounding of potentials at AC 1000 V, DC 1500 V (or higher) according to EPIP see EHS-FIR-100 | EHS-FIR-102 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-91
|  | Cable installations | The general design rule for the facility is that cables shall not be spliced | EHS-FIR-173 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-104
|  | LV Power Supply - Loads | H09 Electrical shall provide C&M-systems with power |  |  | ESS-0083112 4.11
|  | Loads CF COMMS room | Demand of electrical loads in CF COMMS rooms |  | SRS - check src | ESS 0053046
|  | Power Outlets CF COMMS room | The CF COMMS rooms need outlets for ELV equipment |  | SRS - check src | ESS 0053046
|  | Power Outlets CF COMMS room | The CF COMMS rooms need outlets for ELV equipment |  | SRS - check src | ESS 0053048
|  | Number and type of power outlets | In addition to outlets for maintenance there is a need of outlets and connections in different sizes. |  | SW? Or ICD | ESS-0145269
Lighting
|  | LV Lighting - Lighting shall be provided | H09 Electrical shall provide lighting according to "Investigaton and strategy regarding industrial lighting", ESS-0027502. |  | SW | Design Manual, ESS-0007857.
|  | LV Lighting - Emergency lighting shall be provided. | H09 Electrial shall provide emergency lighting with emergency lighting installed throughout the facility. The emergency lighting will be power supplied from the back-up power system. |  |  | Fire Safety Strategy Report, ESS-002381, section 9.7
|  | Emergency lighting lux | H09 Electrical shall provide emergency lighting of minimum 15lux. |  |  | Fire Safety Strategy Report, ESS-002381, section 9.8
|  | Warning lights stack | Ventilation stack shall be equipped with warning lights if TSFS 2010:155 sets these requirements |  |  | ESS-0083112 4.11
|  | General lighting - access route | Indoor access route general lighting strength shall be minimum 100 lux | EHS-FIR-067 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-82
|  | General lighting - separate circuits | Every other source of general lighting in access routes shall be powered by separate circuits (fuses). fuse-boxes and earth to ground breakers. | EHS-FIR-068 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-83
Grounding
|  | Lightning protection system | H09 electrical shall proivde lightning protection mesh will be installed on the roofs where required based on the risk analysis described in standard. Lightning protection mesh on roofs properties is to be decided based on results from risk analysis. Risk analysis in H09 ESSxxxx.
|  | Provide lightning protection. | H09 Electrical shall install lightning protection system of class LPS2.
|  | Grounding Hazardous areas | All installations in HAZARDOUS AREAS shall have potential equalization | EHS-EXP-113 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-133
|  | Grounding exposed parts | EXPOSED PARTS shall be connected to the equipotential bonding system | EHS-EXP-119 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-134
|  | Grounding extraneous conductive parts | Extraneous conductive parts shall be connected to the equipotential bonding system | EHS-EXP-125 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-135
|  | Grounding earthing point | The potential equalization system of a HAZARDOUS AREA shall include at least one earthing point of all armour and screens of cables in the HAZARDOUS AREA, even if the earthing points are situated outside of the HAZARDOUS AREA | EHS-EXP-131 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-136
|  | Lightning Protection | All ESS facilities shall be protected by Lightning Protection Level LPS II (2) in standard SS-EN 62305-3, or better | EHS-ELC-001 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-49
|  | Hazardous voltage | All touchable metallic construction parts (e.g. between electrical cubicles and metallic fences or between electrical instruments and other metallic constructions such as pipes, cable ladders and ventilation ducts), shall be grounded so that people in the facilities will not come in contact with hazardous voltage (more than 50 V), based on measured resistance for all touchable metallic construction parts in ratio to "grounding" shall whitstand dimensioned and actual fault short circuit current of 24 kA, 1 sec (design 20 kA x 120 %=24 kA) and 50 kA (peak) from the electrical grid or actual fault short circuit current from other electrical equipment. | EHS-ELC-007 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-50
|  | Short circuit resistance | All metallic parts which are part of the grounding system (e.g. iron bars, main ring conductors) shall whitstand dimensioned and actual fault short circuit current of 24 kA, 1 sec (design 20 kA x 120 %=24 kA) and 50 kA (peak) from the electrical grid or actual fault short circuit current from other electrical equipment. Note that the metallic parts shall withstand both thermical and mechanical forces from the fault short circuit current. | EHS-ELC-013 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-51
|  | Grounding standard | Grounding shall comply with grounding system TN-S | EHS-ELC-019 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-52
|  | Overvoltage protection | An overvoltage protection system shall be implemented on LV- and HV systems. (According to SS-EN 61643-11) | EHS-ELC-046 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-58
Extra Low Voltage
|  |  | General requirements specified for Extra Low Voltage systems see System Requirements at Site Infrastructure level, ESS-0045088 DM--SR-TBSIDD----System Requirements ELV. |  |  | ESS-0045088
Fire Alarm System
|  |  | General requirements specified for Fire Alarm systems and evacuation alarm system see System Requirements at Site Infrastructure level, ESS-0045084 DM--SR-TBSIDD----System Requirements Fire Alarm System. |  |  | ESS-0045084
|  | Fire alarm to SMR | All fire alarms shall be transmitted to the Security Monitor room | EHS-SEC-012 |  | ESS-0066475 | [12 empty] | SRH09-152
|  | Fire alarm to MCR | All fire alarms shall be transmitted into the Main Control room | EHS-SEC-021 |  | ESS-0066475 | [12 empty] | SRH09-153
|  | Detection coverage | Automatic fire alarm shall cover all areas of the facility in compliance with SBF 110:7 110:6 | EHS-FIR-045 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-75
|  | Fire alarm to SOS | The fire alarm shall be directly connected to the municipal SOS alarm center | EHS-FIR-046 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-76
|  | Emergency Response Team | Fire alarm equipment shall be connected to SOS with an alarm storage delay of 3 to 5 minutes | EHS-FIR-047 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-77
|  | Radiation resistant detectors | Fire detection equipment shall retain its performance for minimum 2 years in areas exposed to ionization radiation | EHS-FIR-050 |  | ESS-0078440/ ESS-0043151 | [12 empty] | SRH09-78
|  | Fire alarm - environment | In the design of the fire alarm system, special consideration shall be given to the nature of the work expected in the Hot work room. |  |  | ESS-0083112 4.11
|  | Fire alarm - environment | Type of fire alarm detection must be chosen according to environment in rooms. (dust, radiation, water, temperature, etc.) |  |  | ESS-0183699
Integrated Security System
|  |  | General requirements specified for Integrated Security systems see System Requirements at Site Infrastructure level, ESS-0045083 DM--SR-TBSIDD----System Requirements Integrated Security System. |  |  | ESS-0045083
|  | Protected area lock | All passages such as gates, doors, culverts etc. through outer surrounding physical perimeter into protected area shall, as a minimum, be locked according to SS-EN 1627:2011 and SS-EN 3522, corresponding to SSF 200, protection class 2. (The standard stipulates lock class 3 but we will supply locks with class 2.) | EHS-SEC-106 |  | ESS-0066475 | [12 empty] | SRH09-155 | OK?? @Magnus, Detta är OK, enligt aggrement. Krav bör även hänvisa till övergripande systembeskrivning SI.
|  | Protected area identification | All persons shall at each time when entering in to protected area be identified as an individual to ensure that the right person is given access to the protected area. (Only via card readers and CCTV) | EHS-SEC-107 |  | ESS-0066475 | [12 empty] | SRH09-156 | OK?? @Magnus, Det är fortfarande oklart vad som gäller vid inpassage tilll "controlled area" Card Reader JA, CCTV troligen?? Notering: OK. Further procedures to ensure controlled and registerad acceess needed. Also see SEC-065??
|  | Protected area access control | All physical entrances in to a protected area by an individual shall be registered in ESS access control system. (Only via card readers and CCTV) | EHS-SEC-108 |  | ESS-0066475 | [12 empty] | SRH09-157 | OK?? @Magnus, Entré skall idag endast utrustas med Card Reader enligt följande notering från ESH. Ok with registration through car readers
|  | Protected area intruder alarm | For all passages such as gates, doors, culverts etc. into proteced areas, an intruder alarm shall be installed. | EHS-SEC-109 |  | ESS-0066475 | [12 empty] | SRH09-158 | OK
|  | Intruder alarm | SSF 130, SSF 140 and SSF 114 standards shall be applied to all intruder alarm installations | EHS-SEC-007 |  | ESS-0066475 | [12 empty] | SRH09-148
|  | Protected area | All passages such as gates, doors, culverts etc. into protected areas shall be connected to an intruder alarm. | EHS-SEC-009 |  | ESS-0066475 | [12 empty] | SRH09-150
|  | Alarm to SMR | All alarms triggered by security systems for physical protection shall be transmitted to the Security Monitor room | EHS-SEC-011 |  | ESS-0066475 | [12 empty] | SRH09-151
|  | Location of Card readers in access control system | Card readers in access control system shall be placed according to card reader drawings found in ESS-0173270 |  |  | ESS-0173270
|  | Door control fire compartments | It shall be possible to monitor the positions of lockable doors and gates in the operations centres, in order to make it easy to verify if fire compartments are broken or not |  |  | ESS-0083112 4.8
|  | Interlock system zones Barrier area | All doors adjacent to the barrier area H09.100.1016 shall be controlled by an interlock system in In order to withhold the under pressure in the rooms on controlled area. An interlock system is needed between doors to H09.100.1010 PASSAGE and to Changing rooms. |  |  | ESS-0183699 |  | Essential
|  | Interlock system Overhead crane hall | In order to withhold the under pressure in the rooms on controlled area. An interlock system is needed for all doors that are in direct contact to the air volume of the overhead crane hall H09.100.1009. |  |  | ESS-0066112 |  | Essential
CCTV System
|  |  | General requirements specified for CCTV System, see System Requirements at Site Infrastructure level, ESS-0045086 DM--SR-TBSIDD----System Requirements CCTV System. |  |  | ESS-0045086
|  | Protected area CCTV | All entrances in to protected area shall be monitored by CCTV. (Entrances in to protected area will be monitored by CCTV accordimg to the physical security agreement.) | EHS-SEC-105 |  | ESS-0066475 | [12 empty] | SRH09-154 | OK?? @Magnus, Följande förtydligande är överenskommet. Entrances in to protected area will be monitored by CCTV accordimg to the physical security agreement. - Vilket idag innebär att entreér skall övervakas med kamera
|  | Protected area identification | All persons shall at each time when entering in to protected area be identified as an individual to ensure that the right person is given access to the protected area. (Only via card readers and CCTV) | EHS-SEC-107 |  | ESS-0066475 | [12 empty] | SRH09-156 | OK?? @Magnus, Det är fortfarande oklart vad som gäller vid inpassage tilll "controlled area" Card Reader JA, CCTV troligen?? Notering: OK. Further procedures to ensure controlled and registerad acceess needed. Also see SEC-065??
|  | Protected area access control | All physical entrances in to a protected area by an individual shall be registered in ESS access control system. (Only via card readers and CCTV) | EHS-SEC-108 |  | ESS-0066475 | [12 empty] | SRH09-157 | OK?? @Magnus, Entré skall idag endast utrustas med Card Reader enligt följande notering från ESH. Ok with registration through car readers
|  | Protected area detection by CCTV | Intrusion in to protected area shall be able to be detected and verified immediately through CCTV. | EHS-SEC-110 |  | ESS-0066475 | [12 empty] | SRH09-159 | OK?? @Magnus, detta är en programmeringsfråga för Stanley. Kameror i anslutning till entrér integreras mot inbrottslarm i detta hus, OK.
|  | Document CCTV | CF shall document the intended function of each camera in the CCTV surveillance system in accordance with the standards SSF1060:2, SS-EN 50132-1:1 and SS-EN 50132-7:2. | EHS-SEC-008 |  | ESS-0066475 | [12 empty] | SRH09-149
Communication Systems
|  |  | General requirements specified for Communication System see System Requirements at Site Infrastructure level, ESS-0045085 DM--SR-TBSIDD----System Requirements Communication System. |  |  | ESS-0045085
Other ELV System
|  |  | General requirements specified for Other ELV systems see System Requirements at Site Infrastructure level, ESS-0045087 DM--SR-TBSIDD----System Requirements Other ELV. |  |  | ESS-0045087
Note on A2: Unique identifier
Note on B2: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on C2: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on D2: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on E2: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID. The child req. is more detailed and specific, it satisfies parts of or the entire parent req. It is also used to link requirements for validation purposes.
Note on F2: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on G2: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on H2: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on I2: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on J2: When the requirement is derived from a risk analysis. The related Risk Id shall be included.
Note on K2: Name of the last reviewer
Note on L2: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on M2: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N2: The expected minimum value for the parameter of interest
Note on O2: The expected nominal value for the parameter of interest
Note on P2: The expected maximum value for the parameter of interest
Note on Q2: S.I. units for the value of interest specification.
Note on R2: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on S2: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on T2: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on U2: Text describing how this requirement shall be verified. Details of how and at when verification activities should be performed. Can be a CHESS reference to Verification Plan.

## Example
Requirement attributes. Help can be obtained by hovering with the mouse over any of the titles of the columns | [18 empty] | These are not requirement attributes.
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Comments
|  | Waste room area | The CUB waste room shall have a minimum area of 9 m² in in order to facilitate handling of waste in connection with the CUB |  |  | ESS-0013188 MoM CUB Meeting 20 | Measurement | Useful | [9 empty] | In work | A02-002 | Measurements of waste room in drawings and at commissioning
|  | Ventilation air flow | The Ventilation in all CUB rooms shall have a minimum air flow of 0,35 l/s /m2 in order to fulfill regulations |  |  | SS-EN1717 | Measurement | Essential | [9 empty] | In work |  | Measurements according to verification plan ESS-0023456
|  | Comply with SS-EN 61936-1 | The High voltage power System shall comply with SS-EN 61936-1 (standards for Power installations exceeding 1 kV) | Si-SyR123 |  | ESS-0012345 | Inspection | Essential | [9 empty] | Approved | PowerRe-14 | Verification of derived requirements (PowerRe-25, PowerRe-27, PowerRe-30)
|  | Climatic and environmental conditions humidity | The H06 indoor climate shall have average value of the relative humidity, measured over a period of 24 h of maximum 95 % in order to minimize the risk of condensation. | PowerRe-14 |  | SS-EN 61936-1 Chapter 4.4.2.1e | Inspection | Essential | [9 empty] | In review | PowerRe-25 | Verification of H06 HVAC req. derived from this req.
ESS …
XXXX
Note on A2: Unique identifier
Note on B2: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on C2: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on D2: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on E2: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID It is also used to link requirements for validation purposes.
Note on F2: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on G2: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on H2: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on I2: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on J2: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on K2: Name of the last reviewer
Note on L2: When the requirement is specific to an operating mode for the So I, the name of the mode shall be specified
Note on M2: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N2: The expected minimum value for the parameter of interest
Note on O2: The expected nominal value for the parameter of interest
Note on P2: The expected maximum value for the parameter of interest
Note on Q2: S.I. units for the value of interest specification.
Note on R2: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on S2: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on T2: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on U2: Text describing how this requirement shall be verified. Can be a CHESS reference to Verification Plan.
Note on D5: This high level requirement is broken down to several system specific requirements
Note on E6: This cell contains a reference to the ID of the parent requirement

## Req. Descript.
Requirement description's template for all types of requirements except interface requirements:
The | [System – who/what does the action]
shall | [Function – what happens e.g. store, update, send data]
the | [System – what is acted upon]
to the | [System – where the output is sent recipient or end state]
At/with | [Performance - frequency and/or quality characteristic]
when | [Event – causes of action; data receipt/user interaction]
unless/even if | [Constraint – business rule or limiting factor]
So that | [Rationale - description of value or benefit is achieved].
Example
The PUMP shall MOVE the COOLENT to the HEAT EXCHANGER at a rate of 500 LITERS PER MINUTE when THE COOLENT TEMPERATURE IS OVER 120C unless THE TEMPERATURE IS OVER 130C WHEN THE RATE WILL BE 600 LITERS PER MINUTE so that HOT COOLENT IS TAKEN AWAY FROM THE TARGET. NB! this example is all inclusive of the template above. Requirement descriptions may or may not be so extensive.
Interface requirement description form (these requirement types are written in pairs):
Your requirement
[System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface].
Your counterparts requirement
[System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].

## Revision history (hidden)
ESS-0002908 SEMP v1.5 | ESS-0002908 SEMP v1.5 | ID | Category | Name | Text |  |  | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX-YYY Interface requirements table view | Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX.SyR-TEMPLATE table view | Object Identifier | Category | Req short test | Req Text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
| New categories |  | Requirement Categories |  |  | "Derived from" is used for linking to requirement on level above | "Allocated to" is used to allocate requirements to next lower SOI (system of Interest) |  | Verification methods | Priority values, used to | [9 empty] | Status values, with "in revision" removed
Functional
| Constraint |  | Functional | [5 empty] | Inspection | Essential | [9 empty] | In work
| Environment |  | Constraint | [5 empty] | Measurement | Useful | [9 empty] | In review
| Radiation safety |  | Interface | [5 empty] | Demonstration | Desirable | [9 empty] | Approved
| Conventional safety |  | Environment | [5 empty] | Analysis | [10 empty] | Released
|  |  | Radiation safety | [16 empty] | Obsolete
| Removed categories |  | Conventional safety
Electrical
Regulatory
Operational
Mainatnance
Structural
Safety
Interface
The attribute "version" is removed in .v5 the only differance to the communicated .v4 at the SE meeting 28 dec 2014. Version was added by mistake…
Several attributes changes i .v6. The attributes marked yellow and that exist in SEMP is only renamed. 3 new attributes is added. "Object heading" to facilitate chapter struction within a DOORS 9.x module. 2 new attributes "Satisfies" and "Satisfy by" to facilitate validation linking and allocation on next level. The value attributes marked orange, is change from "real" to "string" to support scientific format. Changes is proposed 2 Feb 2015 to simpfy requirement export, import and mangement in "Excel" format only. Other document style is not supported by this template. This template will provide a unified import, internal and export format.
Changes in v.7: #1 The attribute Category have a reduced number of categories: Proposed new set is Functional; Constraints; Environment; Radiation Safety; Conventional safety; Removed is Electrical; Regulatory; Operational; Maintanance; Structural; Safety; Interface. #2 The attribute "Satisfies" is exchanged to "derived from". "Satisfy" by is replaced by "Allocated to", which is added to simplify allocation to next level and used for verifying "derived from links" In revision is removed from the Status attribute
Changes in v.8: #1 Value "Interface" added in the attribute Category. Interface was omitted by mistake in v.7 #2 The attribut "Responsible" is removed
Changes in v.9 #1 The attribute "req id" is replaced by "Object Identifier"red color above. Rationale is that only DOORS generated ID shall be used as unique requirement ID. MagicDraw generated IDs will not be used in DOORS for new added requirements in the future. #2 Minor editorial changes in revision history tab and cell A2 ands B2 with references to DOORS module is removed in the DOORS Req. format tab not to be mistaken for a attribute.
Note on C1: Unique identifier
Note on D1: • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on E1: Name of the parameter defining the performance
Note on F1: Textual description of the requirement
Note on I1: Trace to a source document, DMS Id shall be mentioned.
Note on J1: Specification of one of the fourth possible verification method
Note on K1: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on L1: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on M1: Name of the last reviewer
Note on N1: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on O1: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on P1: The expected minimum value for the parameter of interest
Note on Q1: The expected nominal value for the parameter of interest
Note on R1: The expected maximum value for the parameter of interest
Note on S1: S.I. units for the value of interest specification.
Note on T1: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on U1: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on G2: A relation attribute to relate this requirement on PBS level n to a requirement on PBS level n-1 which it satisfy. It is use to link requirements for validation purposes.
Note on H2: A relation attribute to relate this requirement on level n to the next system node that satify this requirement on PBS level n+1. It is used for allocation purposes.
Note on P2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on Q2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on R2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS