## First Sheet
DM--ID-DEPDDDH09-Common Systems ICD.xls
|  | Name | Role/Title
| Owner | Tobias Hörnfeldt | Requirement engineer
| Reviewers | Per Persson Boris Kildetoft Patrik Persson Martin Hanson Lisa Ljungberg Magnus Lindström Magnus Leonardsson Frank Kezerle Ronny Sjöholm Fredrik Österberg Ulrika Agnvik | Waste manager Building owner System owner HVAC System owner Process System owner Electrical HVAC/Mechanical Engineer System Manager el System owner architectural and structural Senior Design Engineer Design Engineer Senior Security Officer
| Approver | Boris Kildetoft | Building owner
Glossary
| Term | Definition
| CWL | Cooling Water Low temp
| DHL | District Heating Low temp
| DIW | Deionized Water
| HDW | Hot Deionized Water
| HW | Domestic hot-water system
| IAR | Compressed Air (instrument)
| LSC | Lead Shielded Container
| SW | Storm Water
| W | Domestic cold-water
| WW | Waste Water
| WWR | Waste water risk
| RWWS | Radiological waste water system
| UPS | Uninterruptible Power Supply
| TLD | ThermoLuminescent Dosimeter
| EPD | Electronic Personal Dosimeter
| REMS | Radiation Environment Monitoring System
| NC | Normaly Closed
| NO | Normaly Opend
Review comments are found in ESS-0154142

## Room configuration
Room# | Room name | Cooling Water Low temp | District Heating Low temp | Deionized Water | Hot Deionized Water | Domestic Hot-Water System | Compressed Air (instrument) | Storm water | Domestic Cold-Water | Waste Water | Waste Water Risk | Radiological Waste Water System | Admin IT? (Y/N) | waste water pipes casted in? | Ventilation/room classification collor | Vent clasification | Direct radiation | Surface contamination | Voltage level equipment [V] | Rated Power [kVA] | Actual Power [kVA] | Responsible
H09.090.1000 | CULVERT | N | N | N | N | N | N | N | N | N | Y | N | N | N | Supervised Green | Unclasified | Green | Green | 230 | 15 | 2 | HVAC
H09.090.1001 | BASEMENT | N | N | N | N | N | Y | N | N | N | N | N | N | N | Red | C2 | Red | Blue | 230 & 400 | 15.5 | 11.5 | PROCESS
H09.090.1002 | STAIR | N | N | N | N | N | N | N | N | N | Y | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0.5 | 0.5 | STRUCTURAL
H09.100.1000 | OUTSIDE | N | N | N | N | N | Y | Y | N | N | N | N | N | N | White | Unclasified | White | White | 230 & 400 | 131 | 55 | EARTH WORKS
H09.100.1001 | GROUTING ROOM | N | N | N | N | N | N | N | N | N | N | Y | Y | N | Red | C2 | Red | Yellow | 230 & 400 | 12.7 | 6.1 | PROCESS
H09.100.1002 | PURIFICATION ROOM L1 | N | N | Y | N | N | Y | N | N | N | N | Y | Y | N | Red | C2 | Red | Blue | 230 & 400 | 55 | 22 | PROCESS
H09.100.1003 | RRS (LSC) | N | N | Y | N | N | Y | N | N | N | N | Y | N | N | Red | C2 | Red | Red | 230 | 0 | 0 | PROCESS
H09.100.1004 | PUMP ROOM | N | N | Y | N | N | N | N | N | N | N | Y | N | Y | Blue | C1 | Yellow | Blue | 230 & 400 | 125.2 | 83.2 | PROCESS
H09.100.1005 | STAIR 1 | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | STRUCTURAL
H09.100.1006 | CLEANING ROOM 1 | N | N | Y | Y | N | N | N | N | N | N | Y | N | N | Blue | C1 | Blue | Blue | 230 | 0.5 | 0.2 | HVAC
H09.100.1007 | TANK ROOM | N | N | Y | Y | N | Y | N | N | N | N | Y | Y | Y | Blue | C1 | Yellow | Blue | 230 | 15.5 | 2.5 | PROCESS
H09.100.1008 | Low intermediate lvl storage | N | N | N | N | N | N | N | N | N | N | N | N | Y | Blue | C1 | Yellow | Yellow | 230 | 0 | 0 | STRUCTURAL
H09.100.1009 | Overhead crane hall | N | N | Y | Y | N | Y | N | N | N | Y | N | Y | Y | Blue | C1 | Blue | Blue | 230 & 400 | 54.4 | 17.4 | STRUCTURAL
H09.100.1010 | PASSAGE | N | N | N | N | N | N | N | N | N | Y | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | STRUCTURAL
H09.100.1011 | SECONDARY OPERATIONS CENTER | N | N | N | N | N | N | N | N | N | N | N | Y | NA | Blue | C1 | Blue | Blue | 230 | 1 | 0.2 | STRUCTURAL
H09.100.1012 | CHEM LAB | N | N | Y | Y | Y | Y | N | Y | N | Y | Y | Y | N | Blue | C1 | Blue | Blue | 230 | 13.1 | 12.4 | ES&H
H09.100.1013 | CHEMICALS | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 16.5 | 11 | HVAC
H09.100.1014 | WATER SAMPLES | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | ES&H
H09.100.1015 | RAD LAB | N | N | N | N | N | Y | N | N | N | N | N | Y | NA | Blue | C1 | Blue | Blue | 230 | 13.7 | 13.7 | HVAC
H09.100.1016 | BARRIER AREA | N | N | N | N | Y | N | N | Y | N | Y | N | Y | NA | Blue | C1 | Blue | Blue | 230 | 2.7 | 1.5 | ES&H
H09.100.1017 | STORAGE | N | N | N | N | N | N | N | N | N | N | N | N | Y | Blue | C1 | Blue | Blue | 230 | 0 | 0 | STRUCTURAL
H09.100.1018 | SHOWER | N | N | N | N | Y | N | N | Y | N | Y | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | HVAC
H09.100.1019 | NUCLIDE CHARACTERISTATION | N | N | N | N | N | N | N | N | N | N | N | Y | Y | Blue | C1 | Blue | Blue | 230 | 2.5 | 2 | ES&H
H09.100.1020 | MAINTENANCE WORKSHOP | N | N | N | N | N | Y | N | N | N | Y | N | Y | N | Blue | C1 | Blue | Blue | 230 & 400 | 20.1 | 4.5 | STRUCTURAL
H09.100.1021 | DECONTAMINATION | N | N | Y | Y | N | Y | N | N | N | Y | Y | Y | N | Blue | C1 | Yellow | Yellow | 230 & 400 | 52.1 | 21.1 | HVAC
H09.100.1022 | HOT WORKS | Y | Y | N | N | N | Y | N | N | N | Y | N | Y | N | Red | C2 | Yellow | Yellow | 230 & 400 | 62.1 | 27 | HVAC
H09.100.1023 | SORTING | N | N | N | N | N | N | N | N | N | Y | N | Y | N | Blue | C1 | Yellow | Yellow | 230 & 400 | 70.3 | 31.8 | ES&H
H09.100.1024 | SHAFT | N | Y | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 400 | 100.2 | 50 | STRUCTURAL
H09.100.1025 | STAIR | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | #REF! | #REF! | STRUCTURAL
H09.100.1051 | SPRINKLER | N | N | N | N | N | N | N | N | Y | N | N | Y | Y | White | Unclasified | White | White | 230 | 0.2 | 0.11 | HVAC
H09.100.1052 | COM | Y | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 0.2 | 0.2 | BMS
H09.100.1053 | EL | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 & 400 | 0.2 | 0.2 | ELECTRICAL
H09.100.1054 | HVAC | Y | Y | N | N | Y | N | N | Y | Y | N | N | Y | Y | White | Unclasified | White | White | 230 & 400 | 12.6 | 10.9 | HVAC
H09.100.1055 | ENTRANCE | N | N | N | N | N | N | N | N | N | N | N | N | NA | White | Unclasified | White | White | 230 | 1 | 0.2 | STRUCTURAL
H09.100.1056 | HWC | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1057 | CLEANING ROOM 2 | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1058 | WC | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1059 | STORAGE | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 2 | 1 | STRUCTURAL
H09.100.1055 | ENTRANCE | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 1 | 0.2 | STRUCTURAL
H09.100.1060 | CIRCULATION | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 0.5 | 0.1 | STRUCTURAL
H09.100.1061 | CHANGING ROOM 1 | N | N | N | N | N | N | N | N | N | N | N | N | NA | White | Unclasified | White | White | 230 | 0 | 0 | STRUCTURAL
H09.100.1062 | WC | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1063 | SHOWER | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1064 | SHOWER | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1065 | WC | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 0 | 0 | HVAC
H09.100.1066 | CHANGING ROOM 2 | N | N | N | N | N | N | N | N | N | N | N | N | NA | White | Unclasified | White | White | 230 | 0 | 0 | STRUCTURAL
H09.100.1067 | KITCHENETTE | N | N | N | N | Y | N | N | Y | Y | N | N | N | Y | White | Unclasified | White | White | 230 | 5.5 | 3.5 | STRUCTURAL
H09.100.1068 | OPERATIONS CENTER | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 10 | 5 | PROCESS
H09.100.1069 | OFFICE | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 10 | 5 | STRUCTURAL
H09.100.1070 | STAFF ROOM | N | N | N | N | N | N | N | N | N | N | N | Y | NA | White | Unclasified | White | White | 230 | 6 | 1.5 | STRUCTURAL
H09.110.1001 | STORAGE | N | N | N | N | N | N | N | N | N | N | N | Y | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | STRUCTURAL
H09.110.1002 | CEMENTATION | N | N | Y | N | Y | Y | Y | Y | Y | N | N | Y | Y | White | Unclasified | White | White | 230 & 400 | 38.35 | 14.6 | ES&H
H09.110.1003 | PURIFICATION ROOM L2 | N | N | Y | N | N | Y | N | N | N | N | N | Y | N | Blue | C1 | Blue | Blue | 230 & 400 | 47 | 32 | PROCESS
H09.110.1004 | STAIR | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | ES&H
H09.110.1005 | STORAGE | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | ES&H
H09.110.1006 | SHAFT | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | HVAC
H09.110.1007 | STORAGE | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Yellow | Yellow | 230 | 0 | 0 | ES&H
H09.115.1000 | STAIR | N | N | N | N | N | N | N | N | N | N | N | N | NA | Blue | C1 | Blue | Blue | 230 | 0 | 0 | STRUCTURAL
H09.115.1001 | UNCONTROLLED HVAC | Y | Y | N | N | Y | N | N | Y | Y | N | N | Y | Y | White | Unclasified | White | White | 230 & 400 | 2.7 | 2.7 | HVAC
H09.115.1002 | CONTROLLED HVAC | Y | Y | Y | Y | N | N | N | N | N | Y | N | Y | Y | Blue | C1 | Blue | Blue | 230 & 400 | 18.7 | 18.7 | HVAC
H09.115.1003 | STACK MONITORING ROOM | N | N | N | N | N | N | N | N | N | N | N | Y | NA | Blue | C1 | Blue | Blue | 230 | 5.3 | 4.9 | ES&H
Note on C27: Tobias Hörnfeldt: Used for the ventilation/evaporator
Note on D29: Tobias Hörnfeldt: Used for the ventilation/evaporator

## Equipment specfics
Room # | Room name | Equipment | Description of equipment | Equipment name | no. Units | Price/unit | In scope? | CF | ES&H | Dimensions HxWxD | Connection point | Voltage [V] | Rated Power [kVA] | Actual Power [kVA] | Diversity factor | Interlock [Yes/No] | UPS Y/N | Generator power Y/N | Mass [kg] | Responsible
H09.090.1000 | Culvert | Process pipes |  |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A | N | N | N | N | N/A | PROCESS
H09.090.1000 | Culvert | Sump | In case a pipe breaks, water will end up in the lowest part of the culvert. |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.090.1000 | Culvert | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.090.1000 | Culvert | Magnetic switches | for door |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | N | N | N/A | Electric
H09.090.1000 | Culvert | Door | Door between green and blue area |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.090.1001 | BASEMENT | Process pipes |  |  |  |  | CF | CF |  |  |  | 230 | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.090.1001 | BASEMENT | Sampling point | To send water for sampling in the fume cupboard in H09.100.1004 |  |  |  |  | CF |  |  |  | N/A | N/A | N/A |  | N | N | N | N/A | PROCESS
H09.090.1001 | BASEMENT | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.090.1001 | BASEMENT | Tank | Waste water tank | H09-TA012 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 20000 | PROCESS
H09.090.1001 | BASEMENT | Resin Tank | For Ion-exchange resin in case of accident in H09.100.1003 | H09-TA013 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N |  | PROCESS
H09.090.1001 | BASEMENT | Level indicator | For level kontrol in the tank. |  | TBD |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.090.1001 | BASEMENT | Sump | In case a the tank is flodded, water will end up in the lowest part of H09.090.1001. To be placed as far away from the resin tank as possible |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.090.1001 | BASEMENT | Pump in sump |  |  | 1 |  | CF |  |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | PROCESS
H09.090.1002 | Stair 0 | Process pipes |  |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.090.1002 | Stair 0 | Sump | In case a pipe breaks, water will end up in the lowest part of the culvert. |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.090.1002 | Stair 0 | Pump in sump |  |  | 1 |  | CF |  |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | HVAC
H09.100.1000 | Outside | Logistics apron areas |  |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | Fenced in area for containers |  |  | 12 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | Lighting for fenced in area for containers | Makes it possible to find the right container, even in the dark. |  | 3 |  | CF | CF |  |  |  | 400 | 2 | 1 |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | parking places with charging stations |  |  | 1 |  | CF | CF |  |  |  | 400 | 11 | 11 |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | parking places with charging stations |  |  | 1 |  | CF | CF |  |  |  | 400 | 11 | 11 |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | parking places with charging stations |  |  | 1 |  | CF | CF |  |  |  | 400 | 11 | 11 |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | accessibility adapted parking place |  |  | 1 |  | CF | CF |  |  |  | 400 | 11 | 11 |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | bicycle stand /Bike Shed | for at least 6 bikes. |  | 1 | 2500 | CF | 2500 |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | EARTHWORKS
H09.100.1000 | Outside | door protection hoops | This is to secure the structural integrity of the building |  | 4 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1000 | Outside | Ladders | To enter, or escape the roof |  | 2 | 400 | CF | 800 |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1000 | Outside | Connection for compressed air | Experience show this is needed for future tents on the north outside of the building |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1000 | Outside | Connection for compressed air | Experience show this is needed for future tents on the D146south outside of the building |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1000 | Outside | Fall protection for workers on the roofs | Environmental instruments on the roof need to be maintained and operated. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1000 | Outside | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Outlet | 1 pcs. 63 A 3 phase outlet next to the north west gate |  | 1 |  | CF | CF |  |  |  | 400 | 20 | 2 |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Outlet | 1 pcs. 63 A 3 phase outlet next to the south east gate |  | 1 |  | CF | CF |  |  |  | 400 | 20 | 2 |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Guard barriers against collision. | This is to secure the structural integrity of the building |  | 4 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1000 | Outside | Sediment basin | Experience show this is needed to handle water from the cement distribution room, if water from this room is sent to normal sewage, the pipes will soon be filed with cement. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1000 | Outside | Card reader |  |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1000 | Outside | Door | Door to access office part. |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1001 | Grouting room | Overhead Crane | a 6.3 ton traverse according to Platoms sugestion. |  | 0 | 21000 | NO |  |  |  |  | 400 | 10.5 | 5 |  |  | N | N | 1950 | ES&H
H09.100.1001 | Grouting room | Mould lifter etc | Things needed for the rooms |  | 0 | 3000000 | NO | 0 |  |  |  | 230 | 2 | 1 |  |  | N | N | 800 | ES&H
H09.100.1001 | Grouting room | Moulds | According to Per. |  | 10 | 1600 | NO |  | 16000 |  |  | N/A | N/A | N/A |  |  | N | N | 50000 | ES&H
H09.100.1001 | Grouting room | Detector for online dose rate measurement | To know how much resin to fill in each mould |  | TBD | n/a | NO |  | ES&H |  |  | 230 | 0.2 | 0.1 |  |  | N | Y | N/A | ES&H
H09.100.1001 | Grouting room | Process Penetrations | The grouting room will have thick walls and needs to be prepared with melded cable entries, and moulded pipe entries. |  | TBD |  | TBD | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1001 | Grouting room | Door | Very thick and heavy door |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | TBD | STRUCTURE
H09.100.1001 | Grouting room | Sump | To stop RWW from exiting the room |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1002 | Purification room | Oil separator | COALESCER | H09-FI001 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Mechanical filter | PARTICLE FILTER | H09-FI002 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | TBD | PROCESS
H09.100.1002 | Purification room | Ultrafiltration | A filter | H09-FI003 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | TBD | PROCESS
H09.100.1002 | Purification room | Connection to ventilation stack |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Ion exchanger filter |  | H09-IE001 | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 3840 | PROCESS
H09.100.1002 | Purification room | Sampling points after each step | with return line to minimize losses due to flushing. |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.100.1002 | Purification room | Level indicator |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1002 | Purification room | Pressure indicator |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.100.1002 | Purification room | Sludge dryer / mould evaporator | The water process system will have two mechanical filters, when they get clogged they are back flushed and the sludge is put in the sludge dryer. |  | 1 |  | CF | CF |  |  |  | 400 | 40 | 20 |  |  | N | N | TBD | PROCESS
H09.100.1002 | Purification room | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1002 | Purification room | Dehumidification & filtering | This is for the air coming from the sludge dryer/mould evaporator |  | 1 |  | CF | CF |  |  |  | TBD | TBD | TBD |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Temperature indicator |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.100.1002 | Purification room | Tank cells | This is used to stop workers from being exposed from radiation from more than one tank at a time |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 129100 | STRUCTURE
H09.100.1002 | Purification room | Spill preventing structure | In case of leakage, the resin shall stay within the tank cell, not contaminate the whole room. |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1002 | Purification room | Resin tank |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 7500 | PROCESS
H09.100.1002 | Purification room | Resin tank |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 7500 | PROCESS
H09.100.1002 | Purification room | blinded flanged nozzles |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | overfill protection |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Water sampler (possible in an other room) |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Level indicators |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1002 | Purification room | Pressure sensor |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.100.1002 | Purification room | Temperature sensor |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | PROCESS
H09.100.1002 | Purification room | connection to ventilation from resin tank |  |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Tank flushing equipment | Enables cleaning of the tank using deionised water |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1002 | Purification room | Channel drain | To stop RWW and resin from exiting the room leads to tanks in the basement. The channel drains shall not be equipped with water lock. |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1003 | RRS (LSC) | Ladder or similar for docking with LSC | A good working position is critical for reducing the number of faulty connections to the LSC |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1003 | RRS (LSC) | Steel door | The door needs to be in quite thick steel |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | 250 | STRUCTURE
H09.100.1003 | RRS (LSC) | Control station | This is placed just outside the LSC room. |  | 1 |  | CF | CF |  |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | PROCESS
H09.100.1003 | RRS (LSC) | Reception station | The LSC shall be possible to be decontaminated in case of mishaps. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | TBD | PROCESS
H09.100.1003 | RRS (LSC) | Particle filters |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1003 | RRS (LSC) | Embarkment | In case mishaps, the resin shall be stoped from entering the overhead crane hall H09.100.1009 and instead be lead it into a sort of container where it can be colected and transported to resin storage tank |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | TBD | PROCESS
H09.100.1003 | RRS (LSC) | Lead shielded transport container |  |  | 1 |  | NO |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | 5000 | ES&H
H09.100.1003 | RRS (LSC) | channel drain | To stop RWW and resin from exiting the room leads to tanks in the basement. The channel drains shall not be equipped with water lock |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1003 | RRS (LSC) | Connection piece to LSC enabling receiving radioactive waste water and or ion resin |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1003 | RRS (LSC) | Connection piece to LSC enable delivering radioactive waste water and ion resin | In chase the grouting room will not be used, there need to be a way to deliver ion resin and radioactive water to the LSC. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1003 | RRS (LSC) | Connection piece to enable receiving radioactive waste water | If a building is sprinkled, and water is on the controlled side, this water will need to be handled in H09, the connection pipe gives us this possibility, without having to use a LSC (witch have small volume). |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1003 | RRS (LSC) | Connection piece to enable delivering of free-released, purified water | In case VA-Syd are unable to receive purified water, this connection piece gives us the possibility to use tank trucks to get rid of the water. This way, the machine dose not have to stop due to trouble at/with VA-Syd. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1004 | Pump room | On-Line Process Monitor | On-Line monitors are designed to continuously, accurately and reliably detect the gamma activity of gaseous or liquid effuent releases from a variety of operational processes |  | 1 |  | Not CF |  |  |  |  | 230 | 0.2 | 0.2 |  |  | TBD | TBD | N/A | PROCESS
H09.100.1004 | Pump room | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1004 | Pump room | Fume hood with local filtering | For sampilng of water. Maximum 1.5 m wide and the hatch may be opened a maximum of 0.5 m in height. It shall be equipped with a local scrubber in order to reduce the corrosion on the ducts. The Scrubber causes a maximum pressure drop of 500kPa. The Fume hood causes a maximum pressure drop of 60Pa. |  | 1 |  | Not CF |  |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | 150 | HVAC
H09.100.1004 | Pump room | Tap | with deionised water for cleaning in the fume cupboard, for cleaning of cupboard and test tubes |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Pump |  |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 11 |  |  | N | N | 229 | PROCESS
H09.100.1004 | Pump room | Particle filter |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1004 | Pump room | Telfer crane (2-ton) | This crane will be needed to move and service pumps |  | 1 | 3900 | CF | 3900 |  |  |  | 400 | 4 | 3 |  |  | N | N | 500 | TRANSPORT
H09.100.1004 | Pump room | Floor drain | To be conected to the fume cupboard |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1004 | Pump room | Floor drain | To be in the lower part of the room |  | 1 |  | CF |  |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | HVAC
H09.100.1004 | Pump room | C&M Network, Data Outlet 2xRJ45 | For data access to on-line process monitor |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | TBD | TBD | N/A | Electric
H09.100.1005 | Stair 1 |  |  |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1006 | Cleaning room 1 | Taps | Equiped with hot and cold deionised water. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | n | n | N/A | PROCESS
H09.100.1006 | Cleaning room 1 | slop basin | For emptying RWW, leads to the sump/channel drain |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1006 | Cleaning room 1 | Locker/shelfs | For storage off cleaning chemicals etc. |  | 1 | 200 | Not CF |  | 200 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1006 | Cleaning room 1 | channel drain | leads to the sump |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1006 | Cleaning room 1 | Sump | To stop RWW from exiting the room |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1006 | Cleaning room 1 | Pump in sump |  |  | 1 |  | CF |  |  |  |  | 230 | 0.5 | 0.2 |  |  | N | N | N/A | HVAC
H09.100.1007 | Tank room | 30m3 tank (process) |  | H09-TA002 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 33000 | PROCESS
H09.100.1007 | Tank room | 30m3 tank (process) |  | H09-TA003 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 33000 | PROCESS
H09.100.1007 | Tank room | 40m3 tank (release) |  | H09-TA007 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 44000 | PROCESS
H09.100.1007 | Tank room | 40m3 tank (release) |  | H09-TA006 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 44000 | PROCESS
H09.100.1007 | Tank room | 120m3 tank (process water buffer) |  | H09-TA004 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 130000 | PROCESS
H09.100.1007 | Tank room | 120m3 tank (process water buffer) |  | H09-TA005 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 130000 | PROCESS
H09.100.1007 | Tank room | Collection tank 5m3 | Collection tankar resin and chemical tank 5 m3 | H09-TA001 | 1 |  | CF | 0 |  |  |  | N/A | N/A | N/A |  |  | N | N | 6000 | PROCESS
H09.100.1007 | Tank room | Tank-connection to ventilation |  |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1007 | Tank room | Tank flushing equipment |  |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1007 | Tank room | blinded flanged nozzles |  |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1007 | Tank room | overfill protection | UPS secured |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1007 | Tank room | Level indicators | UPS secured |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1007 | Tank room | Pressure sensors | UPS secured |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1007 | Tank room | Temperature sensors | UPS secured |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | Y | Y | N/A | PROCESS
H09.100.1007 | Tank room | Piping, valves |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1007 | Tank room | Particle filters | Ventilation via hepa filters etc. |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1007 | Tank room | slop basin | water to be sent to the channel drains |  |  |  |  | CF |  |  |  | N/A | N/A | N/A |  | N | N | N | N/A | HVAC
H09.100.1007 | Tank room | taps | with hot and cold deionised water |  |  |  |  | CF |  |  |  | N/A | N/A | N/A |  | N | N | N | N/A | PROCESS
H09.100.1007 | Tank room | Channel drain | For transport of water to the sump |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1007 | Tank room | Sump | To stop RWW from exiting the room |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1007 | Tank room | Pump in sump | Note that it should be possible to change to which tank water from this room is pumped, as it may be extremely large quantities and it may not per default be RWW. |  | 1 |  | CF |  |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | HVAC
H09.100.1007 | Tank room | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1008 | Low intermediate lvl storage | Pallet racks, Modullådor etc. |  |  |  |  | Not CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | 519760 | ES&H
H09.100.1009 | Overhead crane hall | Taps | with hot and cold deionised water |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1009 | Overhead crane hall | sink | Water are transported to the channel drain / sump |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1009 | Overhead crane hall | 20 ton overhead crane + accessories | This will be sufficient to handle lifting the moulds to the transport vehicle, and is sufficient from the components from AD. Mauritz.Lindgren@konecranes.com |  | 1 | 60000 | CF | 60000 |  |  |  | 400 | 10 | 5 |  |  | N | N | 8450 | TRANSPORT
H09.100.1009 | Overhead crane hall | collision guard | To stop the forklift fromdestroying the walls. |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Weight measuring equipment to the crane | ESS is only allowed to hold a limited weight of radioactive waste, so it is important to be able to know the weight of each large component. |  | 1 | 4000 | Not CF |  | 4000 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | TRANSPORT
H09.100.1009 | Overhead crane hall | Category 1 rope or specially designed low-torque rope to the crane. | Normally ropes used in cranes are twisting, this makes the mould twist in it´s position, and makes it hard to put it down strait after it has been lifted. A Category 1 rope will not twist the load. Mauritz will be able to answer on Thursday. |  | 1 | Mauritz | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | TRANSPORT
H09.100.1009 | Overhead crane hall | Swivel | Another way to stop the load from twisting. |  | 1 | Mauritz | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | 500 | TRANSPORT
H09.100.1009 | Overhead crane hall | Mould lifter | Special tool to use with the overhead crane |  | 1 | 50000 | Not CF |  | 50000 |  |  | 230 | 2 | 1 |  |  | TBD | TBD | 1000 | ES&H
H09.100.1009 | Overhead crane hall | Emergency stops for overhead crane |  |  | TBD |  | CF | CF |  |  |  | 24 | 0.1 | 0.1 |  |  | N | N | N/A | TRANSPORT
H09.100.1009 | Overhead crane hall | Runoff to drain sumps | Protecting water from flowing to adjacent rooms or outside the H09. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1009 | Overhead crane hall | compactor | For compacting soft things. Footprint ca 6.5X2.2 m needs at leest 8x2.2 m to operate |  | 1 | 50000 | Not CF |  | 50000 |  |  | 400 | 5 | 3 |  |  | N | N | 20000 | ES&H
H09.100.1009 | Overhead crane hall | C2 Ventilation connection | Ventilation connection to allow for controlled filtered ventilation of the compactor air. IT shall also be possible to modify the connection to support temporary C2-ventilation in tents, in case large and contaminated waste components needs to be treated inside the overhead crane hall. |  | 1 | [14 empty] | HVAC
H09.100.1009 | Overhead crane hall | C2 Ventilation connection | Ventilation connection to allow C2-ventilation in tents, in case large and contaminated waste components needs to be treated inside the overhead crane hall. |  | 1
H09.100.1009 | Overhead crane hall | Smear sample analyser | NT200 from Nutronic is a good instrument for this usage |  | 1 | 11000 | Not CF |  | 11000 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | 60 | ES&H
H09.100.1009 | Overhead crane hall | Hand held scintillator alpha and beta detector | RadEye™ AB100 Alpha-Beta Contamination Monitor From Thermo Scientific is a good instrument for this usage Nuklex.se |  | 1 | 2809 | Not CF |  | 2809 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1009 | Overhead crane hall | QR-code printer |  |  | 1 | 451 | Not CF |  | 451 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | ES&H
H09.100.1009 | Overhead crane hall | EMERGENCY EXITs |  |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Floor drains | Stop water to exiting the house, leads it to TA012 |  | 2 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Forklift | Toyota Traigo80-50 - eldriven (80V) 4-hjulig motviktstruck including charging statoin. |  | 1 | 50990 | Not CF |  | 50990 |  |  | N/A | N/A | N/A |  |  | N | N | 5930 | TRANSPORT
H09.100.1009 | Overhead crane hall | Forklift charger | Ventilation of forklift while charging. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1009 | Overhead crane hall | Forklift charger | Small 32A box on the side of the wall. |  | 1 |  | CF | CF |  |  |  | 400 | 20 | 4 |  |  | N | N | N/A | Electric
H09.100.1009 | Overhead crane hall | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 3 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1009 | Overhead crane hall | HVAC equipment | 4 Air curtains | HWS01-ACU001 | 4 |  | CF |  |  |  |  | 230 | 2 | 2 |  |  | N | N | N/A | HVAC
H09.100.1009 | Overhead crane hall | C&M Network, Data Outlet 2xRJ45 | For overhead cranes |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1009 | Overhead crane hall | C&M Network, Data Outlet 2xRJ45 | For registration station |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1009 | Overhead crane hall | Magnetic switches | for door |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1009 | Overhead crane hall | Door | Door for access from/to outside |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Magnetic switches | for door |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1009 | Overhead crane hall | Door | Door for access from/to outside |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Magnetic switches | For gate |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1009 | Overhead crane hall | Gate | Door for access from/to outside |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1009 | Overhead crane hall | Magnetic switches | For gate |  |  |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1009 | Overhead crane hall | Gate | Door for access from/to outside |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1010 | PASSAGE | Shielding block | Shields the RAD LAB room H09-100.1015 |  | 1 | 6000 | CF |  | 6000 |  |  | N/A | N/A | N/A |  |  | N | N | 3800 | SEC
H09.100.1010 | PASSAGE | Electric equipment | Electric cabinet servicing equipment in H09.100.1020 - 32 etc. |  | 1 | [6 empty] | 400 | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1010 | PASSAGE | C&M Network, Data Outlet 2xRJ45 | For data transport to electrical cabinet |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1011 | SECONDARY OPERATIONS CENTRE | Screeners, safety valve etc. |  |  |  |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1011 | SECONDARY OPERATIONS CENTER | C&M Network, Data Outlet 2xRJ45 | For data transport |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1011 | SECONDARY OPERATIONS CENTER | Outlet workplace | 2 pcs 10 A 1 phase |  | 1 |  | CF | CF |  |  |  | 230 | 1 | 0.2 |  |  | n | n | N/A | Electric
H09.100.1012 | CHEM LAB | Taps | with hot and cold deionised water |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1012 | CHEM LAB | sink | Water are transported to the channel drain / sump |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1012 | CHEM LAB | eye wash and emergency shower | With hot and cold mixed tap water, floor handle etc |  | 1 | 1000 | CF | 1000 |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1012 | CHEM LAB | computers |  |  | 3 | 5000 | Not CF |  | 15000 |  |  | 230 | 0.5 | 0.3 |  |  | N | N | N/A | ES&H
H09.100.1012 | CHEM LAB | fume hoods with local filtering | Each fume hood may be maximum 1.5 m wide and the hatch may be opened a maximum of 0.5 m in height. Each fume hood shall be equipped with a local scrubber in order to reduce the corrosion on the ducts. The Scrubber causes a maximum pressure drop of 500kPa. The Fume hood causes a maximum pressure drop of 60Pa. Only one fume hood at the time is to be opened with running ventilation. |  | 2 | 4500 | Not CF |  | 9000 |  |  | 230 | 1 | 1 |  |  | N | N | 450 | HVAC
H09.100.1012 | CHEM LAB | Ventilated Chemicals Storage Lockers |  |  | 1 | 1336 | Not CF |  | 1336 |  |  | 230 | 1 | 0.5 |  |  | N | N | 500 | HVAC
H09.100.1012 | CHEM LAB | QR-code printer |  |  | 1 | 451 | Not CF |  | 451 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | ES&H
H09.100.1012 | CHEM LAB | Channel drain | Transports water to sump |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1012 | CHEM LAB | Sump | To stop RWW from exiting the room |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1012 | CHEM LAB | Pump in sump |  |  | 1 |  | CF | CF |  |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | HVAC
H09.100.1012 | CHEM LAB | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1012 | CHEM LAB | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1012 | CHEM LAB | Outlet workplace | 15 pcs. 16 A 1 phase outlets 2 pcs. 16 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 10 | 10 |  |  | N | N | N/A | Electric
H09.100.1013 | Chemicals | Ventilated Chemical storage lockers | Special ventilation needed |  | 3 | 1336 | Not CF |  | 4008 |  |  | 230 | 16.5 | 11 |  |  | N | N | 500 | HVAC
H09.100.1014 | Water Sampels | Shelves/lockers | Samples need to be taken from all released water and archived for the future |  | 6 | 100 | Not CF |  | 600 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1015 | RAD LAB | storage lockers |  |  | 6 | 400 | Not CF |  | 2400 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1015 | RAD LAB | working benches |  |  | 2 | 400 | Not CF |  | 800 |  |  | N/A | N/A | N/A |  |  | N | N | 100 | ES&H
H09.100.1015 | RAD LAB | HPGe-detectors for gamma spectroscopy | Enables to see the different gamma emitters in a specimen, including mockup and software |  | 1 | 20000 | Not CF |  | 20000 |  |  | 230 | 2 | 2 |  |  | N | N | N/A | ES&H
H09.100.1015 | RAD LAB | Outlet workplace | 15 pcs. 16 A 1 phase outlets 2 pcs. 16 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 10 | 10 |  |  | N | N | N/A | Electric
H09.100.1015 | RAD LAB | Owen | For making samples |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 1 | 1 |  |  | N | N | N/A | ES&H
H09.100.1015 | RAD LAB | Computers |  |  | 3 | 4000 | Not CF |  | 12000 |  |  | 230 | 0.2 | 0.2 |  |  | N | N | N/A | ES&H
H09.100.1015 | RAD LAB | Smear test instrument for 12 samples | NT900 from Nutronic is a good instrument for this usage |  | 1 | 42000 | Not CF |  | 42000 |  |  | 230 | 0.2 | 0.2 |  |  | N | N | 1000 | ES&H
H09.100.1015 | RAD LAB | Gas cylinder | Flow gas to smear test instrument |  | 1 | 1500 | Not CF |  | 1500 |  |  | N/A | N/A | N/A |  |  | N | N | 500 | ES&H
H09.100.1015 | RAD LAB | Smear test instrument for 1 sample | NT200 from Nutronic is a good instrument for this usage |  | 1 | 11000 | Not CF |  | 11000 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | 55 | ES&H
H09.100.1015 | RAD LAB | Liquid Scintillation Counter | A beta detector instrument for measuring of water samples |  | 1 | 50000 | Not CF |  | 50000 |  |  | 230 | 0.2 | 0.2 |  |  | N | N | 60 | ES&H
H09.100.1015 | RAD LAB | Handheld dose rate instrument | RadEye™ AB100 Alpha-Beta Contamination Monitor From Thermo Scientific is a good instrument for this usage Nuklex.se |  | 1 | 2809 | Not CF |  | 2809 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1015 | RAD LAB | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1015 | RAD LAB | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1016 | BARRIER AREA | Taps | It is important that the workers have clean hands before monitoring. (W and HW from HVAC) |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1016 | BARRIER AREA | Sink | It is important that the workers have clean hands before monitoring. |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1016 | BARRIER AREA | Channel drains | stop the water to enter canging room 1 and 2 |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1016 | BARRIER AREA | Wall Mounted Gowning Racks | To hang the coveralls on, so the workers can reuse the coveralls and do not need to take a new every time they enter. |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1016 | BARRIER AREA | Lockers for storing of new coveralls and shoes | For new coveralls and shoes |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1016 | BARRIER AREA | Fire rated partitioning | This is the physical boundary between the controlled and uncontrolled area, they have different ventilation and it is therefor good if they are in different fire cells (remark by Fredrik Jörud) |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1016 | BARRIER AREA | Personal portal contamination monitor (UPS secured) | Primary monitor. To ensure that contamination is not spread outside the controlled area. UPS kicks in and provides electrical power for at least 2 hours after power failure. (this gives a margin, as they have significantly less capacity after a couple of years) |  | 1 | 100000 | Not CF |  | 100000 |  |  | 230 | 0.3 | 0.3 |  |  | Y | TBD | 1000 | ES&H
H09.100.1016 | BARRIER AREA | Personal portal contamination monitor (UPS secured) | Secondary monitor. To ensure that contamination is not spread outside the controlled area. UPS kicks in and provides electrical power for at least 2 hours after power failure. |  | 1 | 100000 | Not CF |  | 100000 |  |  | 230 | 0.3 | 0.3 |  |  | Y | TBD | 450 | ES&H
H09.100.1016 | BARRIER AREA | Personal portal contamination monitor (UPS secured) | Secondary monitor. To ensure that contamination is not spread outside the controlled area. UPS kicks in and provides electrical power for at least 2 hours after power failure. |  | 1 | 100000 | Not CF |  | 100000 |  |  | 230 | 0.3 | 0.3 |  |  | Y | TBD | 450 | ES&H
H09.100.1016 | BARRIER AREA | Gammabox | For monitoring tools, screeners etc. that has been on controled area |  | 1 | 100000 | Not CF |  | 100000 |  |  | 230 | 0.3 | 0.3 |  |  | N | N | 1000 | ES&H
H09.100.1016 | BARRIER AREA | EPD system (UPS secured) | The EPD should be connected to the personal portal contamination monitor if possible. UPS kicks in and provides electrical power for at least 2 hours after power failure. (this gives a margin, as they have significantly less capacity after a couple of years) |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | TBD | N/A | ES&H
H09.100.1016 | BARRIER AREA | EPD system (UPS secured) | The EPD should be connected to the personal portal contamination monitor if possible. UPS kicks in and provides electrical power for at least 2 hours after power failure. (this gives a margin, as they have significantly less capacity after a couple of years) |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | TBD | N/A | ES&H
H09.100.1016 | BARRIER AREA | EPD system (UPS secured) | The EPD should be connected to the personal portal contamination monitor if possible. UPS kicks in and provides electrical power for at least 2 hours after power failure. (this gives a margin, as they have significantly less capacity after a couple of years) |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | TBD | N/A | ES&H
H09.100.1016 | BARRIER AREA | Baskets on wheels for collection of old coveralls/shoes | For used (dirty) coveralls and shoes. |  | 3 | 150 | Not CF |  | 450 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1016 | BARRIER AREA | Shoe benches with inbuilt shoe stand | This is the boundary where the workers remove there shoes on the inside and go over to the other side waring there coveralls (and socks) |  | 2 | 400 | Not CF |  | 800 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1016 | BARRIER AREA | GPN Network, Data Outlet 2xRJ45 | For data transport to portal monitors |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1016 | BARRIER AREA | GPN Network, Data Outlet 2xRJ45 | For data transport to portal monitors |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1017 | STORAGE | Shelfs/lockers | For new coveralls and shoes |  | 3 | 300 | CF | CF | 900 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1018 | SHOWER | Locker | For new coveralls and shoes |  | 1 | 300 | CF | CF | 300 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1018 | SHOWER | Shower and floor drain | For showering with W and HW |  | 1 | 300 | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1018 | SHOWER | basket on wheels | For used (dirty) coveralls and shoes. |  | 1 | 150 | Not CF |  | 150 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | HPGe-detector | With ISOCS instrumentation |  | 1 | 20000 | Not CF |  | 20000 |  |  | 230 | 1 | 1 |  |  | N | N | N/A | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | rotating plane + weighing scale with QR-code printer | In waste form characterisation the waste form must be rotated to enable measurement from different directions. This is possible designed as recessed into the floor |  | 1 | 5000 | Not CF |  | 5000 |  |  | 230 | 0.5 | 0.5 |  |  | N | N | N/A | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Room for weighing scale | weighing scale and rotating plane |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Detecor and instrumentation | for making the caracterisation |  | TBD |  | Not CF |  |  |  |  | 230 | 1 | 0.5 |  |  | N | N | N/A | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Lead sheading | To shield the detector |  | 1 | 4000 | Not CF |  | 4000 |  |  | N/A | N/A | N/A |  |  | N | N | 60 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Colimator hole in the DOOR | To enable measuring of large objects in the overhead crane hal H09.100.1009 |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1019 | NUCLIDE CHARACTERISTATION | Collimator |  |  | 1 | 100 | Not CF |  | 100 |  |  | N/A | N/A | N/A |  |  | N | N | 500 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Rail track |  |  | 1 | 500 | Not CF |  | 500 |  |  | N/A | N/A | N/A |  |  | N | N | 500 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Rail car |  |  | 1 | 1000 | Not CF |  | 1000 |  |  | N/A | N/A | N/A |  |  | N | N | 100 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Mould transport system |  |  | 1 |  | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | TBD | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Later assembled wall |  |  | 1 |  | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | 32600 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | Heavy door in steel |  |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | 14000 | ES&H
H09.100.1019 | NUCLIDE CHARACTERISTATION | GPN Network, Data Outlet 2xRJ45 | For data transport from analys equipment |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1020 | MAINTENANCE WORKSHOP | Work benches |  |  | 3 | 400 | Not CF |  | 1200 |  |  | N/A | N/A | N/A |  |  | N | N | 300 | ES&H
H09.100.1020 | MAINTENANCE WORKSHOP | Mechanical tools | Hammers, Vice, Files, Torque wrenches, Screwdrivers, etc. |  | 1 | 500 | Not CF |  | 500 |  |  | 230 | 1 | 0.5 |  |  | N | N | 500 | ES&H
H09.100.1020 | MAINTENANCE WORKSHOP | Pillar drill and drill bits |  |  | 1 | 700 | Not CF |  | 700 |  |  | 400 | 1.1 | 0.5 |  |  | N | N | 500 | ES&H
H09.100.1020 | MAINTENANCE WORKSHOP | Metal lathe | May be moved to a later investment |  | TBD |  | Not CF |  | ES&H |  |  | 400 | 3 | 1.5 |  |  | N | N | 1000 | ES&H
H09.100.1020 | MAINTENANCE WORKSHOP | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1020 | MAINTENANCE WORKSHOP | Channel drain | Transports water to sump |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1020 | MAINTENANCE WORKSHOP | Sump | To stop RWW from exiting the room |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1021 | DECONTAMINATION | Taps | Hot and cold deionised water |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1021 | DECONTAMINATION | Sink |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1021 | DECONTAMINATION | Industrial component washing machine | Using deionised water for decontamination (Fagerström) Relese conected to RWWS |  | 1 | 24000 | Not CF |  | 24000 | 1.5 x 1 x 1.2 |  | 400 | 12 | 6 |  |  | N | N | 4000 | ES&H
H09.100.1021 | DECONTAMINATION | Wheel blaster | "slungbläster" (Fagerström) |  | 1 | 550000 | Not CF |  | 550000 |  |  | 400 | 10 | 5 |  |  | N | N | 3000 | ES&H
H09.100.1021 | DECONTAMINATION | C2 Ventilation connection | Ventilation connection to allow C2-ventilation of the wheel blaster. |  | 1 | [14 empty] | HVAC
H09.100.1021 | DECONTAMINATION | High pressure washer | Using deionised water for decontamination (Fagerström) Relese conected to RWWS |  | 1 | included above | Not CF |  | ES&H |  |  | 400 | 10 | 5 |  |  | N | N | 3000 | ES&H
H09.100.1021 | DECONTAMINATION | Dry blasting glove box | Using sand or glass to blast contaminated parts. Function may be covered by above components. (Fagerström) |  | 1 | included above | Not CF |  | ES&H |  |  | 400 | 5 | 3 |  |  | N | N | 2000 | ES&H
H09.100.1021 | DECONTAMINATION | C2 Ventilation connection | Ventilation connection to allow C2-ventilation of the Dry blasting glove box |  | 1 | [14 empty] | HVAC
H09.100.1021 | DECONTAMINATION | Smaller tools like files, brushes, wire brushes |  |  | 1 | 1000 | Not CF |  | 1000 |  |  | N/A | N/A | N/A |  |  | N | N | 500 | ES&H
H09.100.1021 | DECONTAMINATION | Work benches |  |  | 3 | 500 | Not CF |  | 1500 |  |  | N/A | N/A | N/A |  |  | N | N | 300 | ES&H
H09.100.1021 | DECONTAMINATION | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1021 | DECONTAMINATION | QR-code printer |  |  | 1 | 451 | Not CF |  | 451 |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | ES&H
H09.100.1021 | DECONTAMINATION | Sump | To stop RWW from exiting the room |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1021 | DECONTAMINATION | GPN Network, Data Outlet 2xRJ45 | For data transport to DECONTAMINATION EQUIPMENT |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1022 | HOT WORKS | Special fire alarm solution | Needs to be able to operate in different modes depending on if hot works are in progress or not. |  | 1 |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | TBD | TBD | N/A | BMS
H09.100.1022 | HOT WORKS | C2 Ventilation connection | Ventilation connection to allow C2-ventilation of Hot Works area |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | Y | N/A | HVAC
H09.100.1022 | HOT WORKS | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1022 | HOT WORKS | Band saw | Mettal cutting band saw |  | 1 | 3450 | Not CF |  | 3450 |  |  | 400 | 7.5 | 5 |  |  | N | N | 800 | ES&H
H09.100.1022 | HOT WORKS | Rescue scissors | To prevent air contamination when cutting smaller objects (hydralic or electrical powerd tool) 700 bar. Glykol, not oil. Sugested a VariPump 12 W 6 SD and a MOBIL SAX ICU 40 A 30 and a stand fixture (The rescue scissor is about 20 kg) for enabling handling them. From hydraulkraft.se |  | 1 | 50000 | Not CF |  | 50000 |  |  | 230 | 1.5 | 1.5 |  |  | N | N | 100 | ES&H
H09.100.1022 | HOT WORKS | Drum compactor | For compacting in drums |  | 1 |  | Not CF |  |  |  |  | 400 | 7 | 3 |  |  | N | N | 500 | ES&H
H09.100.1022 | HOT WORKS | Work benches |  |  | 2 | 400 | Not CF |  | 800 |  |  | N/A | N/A | N/A |  |  | N | N | 200 | ES&H
H09.100.1022 | HOT WORKS | Circular saw |  |  | 1 | 2000 | Not CF |  | 2000 |  |  | 400 | 1.1 | 0.5 |  |  | N | N | N/A | ES&H
H09.100.1022 | HOT WORKS | C2 Ventilation connection | Ventilation connection to allow C2-ventilation of circular saw |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | Y | N/A | HVAC
H09.100.1022 | HOT WORKS | Blow torcher | For cutting |  | 1 |  | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1022 | HOT WORKS | Flame/plasma/laser-cutting | For cutting, may be moved to a later investment |  | 1 | 2700 | Not CF |  | 2700 |  |  | 400 | 30 | 15 |  |  | N | N | 1500 | ES&H
H09.100.1023 | SORTING | Shredder | For reducing the size of scrap metal (Fagerström) |  | 1 | 580000 | Not CF |  | 580000 | 3.6 x 2.5 x 2.5 |  | 400 | 35 | 17.5 |  |  | N | N | 700 | ES&H
H09.100.1023 | SORTING | C2 Ventilation connection | Ventilation connection to allow C2-ventilation of Shredder |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | Y | N/A | HVAC
H09.100.1023 | SORTING | Overhead Crane | a 6T lift |  | 1 | 6000 | CF | 6000 |  |  |  | 400 | 5.5 | 3 |  |  | N | N | 2000 | TRANSPORT
H09.100.1023 | SORTING | Movable shielding |  |  | 10 | 500 | Not CF |  | 5000 |  |  | N/A | N/A | N/A |  |  | N | N | 10000 | ES&H
H09.100.1023 | SORTING | sorting station | Where incoming waste is sorted, berglövslådor/modullådor |  | 1 | 6000 | Not CF |  | 6000 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1023 | SORTING | Transport containers | vitrea.se will be able to provide this, if we know the sizes. |  | 10 | 0 | Not CF |  | 0 |  |  | N/A | N/A | N/A |  |  | N | N | TBD | ES&H
H09.100.1023 | SORTING | Movable Shielded Glove Box Isolator | (Fagerström) |  | 1 | 290000 | Not CF |  | 290000 |  |  | 400 | 2 | 2 |  |  | N | N | 1500 | ES&H
H09.100.1023 | SORTING | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.100.1023 | SORTING | Robotic arm | With camera mounted on the arm, and a detector to sort more radiating waste without exposing the workers. (Fagerström) |  | 1 | 350000 | Not CF |  | 350000 |  |  | 400 | 2 | 1.5 |  |  | N | N | TBD | ES&H
H09.100.1023 | SORTING | operation station | To control the robot arm (Fagerström) |  | 1 | in above | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.5 |  |  | N | N | TBD | ES&H
H09.100.1023 | SORTING | Waste compaction in mould- press | For compacting waste into moulds. (Fagerström) |  | 1 | 120000 | Not CF |  | 120000 |  |  | 400 | 10 | 5 |  |  | N | N | 1000 | ES&H
H09.100.1023 | SORTING | Shielded storage box | box built up of concrete and with space for 4 moulds and with a motor operated lid or steel cover and serviced by the robotic arm |  | 1 | 50000 | Not CF |  | 50000 |  |  | N/A | N/A | N/A |  |  | N | N | TBD | ES&H
H09.100.1023 | SORTING | Handheld dose rate instrument | RadEye™ AB100 Alpha-Beta Contamination Monitor From Thermo Scientific is a good instrument for this usage Nuklex.se |  | 1 | 2809 | Not CF |  | 2809 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1023 | SORTING | Scalar with QR-printer |  |  | 1 | 600 | Not CF |  | 600 |  |  | 230 | 0.3 | 0.3 |  |  | N | N | N/A | ES&H
H09.100.1023 | SORTING | QR-reader |  |  | 1 |  | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1023 | SORTING | GPN Network, Data Outlet 2xRJ45 | For data transport to robotic arm control station |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1023 | SORTING | Sump | To stop RWW from exiting the room |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1023 | SORTING | Taps | Hot and cold deionised water |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.100.1024 | SHAFT | HVAC PIPES |  |  |  |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1024 | SHAFT | Tritium boiler | This is the only way to get rid of tritium today, how ever new process are on the way, and we need to make space for them, as SSM will surely put new requirements once there are new possibilities for taking care of tritium |  | 1 |  | CF | CF |  |  |  | 400 | 100 | 50 |  |  | N | N | 10000 | PROCESS
H09.100.1025 | STAIR | Stair |  |  | 1 |  | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1051 | SPRINKLER | Alarm valve Floor switch | 230V, 10A |  | 1 |  | CF |  |  |  |  | 230 | 0.1 | 0.1 |  |  | Y | Y | N/A | HVAC
H09.100.1051 | SPRINKLER | Valves etc. | According to fire regulations HVAC will handle this |  | TBD |  | CF |  |  |  |  | 230 | 0.1 | 0.01 |  |  | Y | Y | N/A | HVAC
H09.100.1051 | SPRINKLER | Floor drain | To be conected to WW. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1051 | SPRINKLER | Stair |  |  | 1 |  | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1052 | COM | ICS rack |  |  | 1 |  | CF | CF |  |  |  | 230 | TBD | TBD |  |  | N | Y | N/A | ICS
H09.100.1052 | COM | ELV rack |  |  | 1 |  | CF | CF |  |  |  | 230 | TBD | TBD |  |  | N | Y | N/A | BMS
H09.100.1052 | COM | IT rack |  |  | 1 |  | CF | CF |  |  |  | 230 | TBD | TBD |  |  | N | Y | N/A | BMS
H09.100.1052 | COM | Security rack |  |  | 1 |  | CF | CF |  |  |  | 230 | TBD | TBD |  |  | N | Y | N/A | ES&H
H09.100.1052 | COM | HVAC equipment | Fan Coil Cooling | CW01-FCU002 | 1 |  | CF | CF |  |  |  | 230 | 0.2 | 0.2 |  |  | N | TBD | N/A | HVAC
H09.100.1053 | EL | Electric equipment | Distribution boards |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | EL
H09.100.1053 | EL | HVAC equipment | Fan Coil Cooling | CW01-FCU001 | 1 |  | CF | CF |  |  |  | 230 | 0.2 | 0.2 |  |  | N | N | N/A | HVAC
H09.100.1053 | EL | C&M Network, Data Outlet 2xRJ45 | For data transport to electric control and monitoring system |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1054 | HVAC | HVAC equipment | Valves, Expansion vessel, Pumps, Heat exchanges etc. |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | HVAC equipment | Hot Water Circulation Pump | HWC01-P001 | 1 | [6 empty] | 230 | 0.1 | 0.1 |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | HVAC equipment | Water Boiler | HW01-WB001 | 1 | [6 empty] | 400 | 9 | 9 |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | HVAC equipment | Cooling, Pumps | CW01-P001/P002 | 2 | [6 empty] | 230 | 1 | 0.5 |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | HVAC equipment | Heating, Pumps | HWS01-P001/P002 | 2 | [6 empty] | 230 | 2.4 | 1.2 |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | HVAC equipment | Heating, Shunt | HWS02-SS001 | 1 | [6 empty] | 230 | 0.1 | 0.1 |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | Sink | Each HVAC room is equipped with a sink for washing hands after work. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1054 | HVAC | C&M Network, Data Outlet 2xRJ45 | For data transport to HVAC control system |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1056 | HWC | WC |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1056 | HWC | SINK |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1057 | CLEANING ROOM 2 | slop basin | For emptying liquid waste |  | 1 | 85 | 85 | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1057 | CLEANING ROOM 2 | Shelfs/lockers | For cleaning equipment and chemicals |  | 1 | 150 | 150 | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1057 | CLEANING ROOM 2 | Floor drain | conected to conventional ww. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1058 | WC | WC |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1058 | WC | SINK |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1059 | STORAGE | Printer | For printing |  | 1 |  | Not CF |  |  |  |  | 230 | 2 | 1 |  |  | N | N | N/A | ES&H
H09.100.1059 | STORAGE | GPN Network, Data Outlet 2xRJ45 | For data transport to printer |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.100.1059 | STORAGE | Shelfs/lockers | For papers etc. |  | 1 |  | Not CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1059 | STORAGE | TABLE | For papers etc. |  | 1 | 1000 | Not CF |  | 1000 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1060 | CIRCULATION | TLD-rack | A place to put TLD when not in use |  | 1 |  | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1060 | CIRCULATION | EPD system (UPS secured) | For activation and initiation of PED |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | Y | N/A | ES&H
H09.100.1055 | ENTRANCE | ACCESS CONTROL | CONTROL OF ACCESS |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | Y | N/A | ICS
H09.100.1055 | ENTRANCE | FIRE CENTRAL | FIRE CENTRAL IN ENTRANCE |  | 1 |  | CF | CF |  |  |  | 230 | 0.5 | 0.1 |  |  | TBD | TBD | N/A | BMS
H09.100.1061 | CHANGING ROOM 1 | Lockers with benches | There shall be at least one locker a worker for storing personal items |  | 10 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1061 | CHANGING ROOM 1 | clothes hanging rack | Visitors do not need a locker, they will use a clothes hanging rack. This is also needed for outwear in case of snow or rain. |  | 4 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1061 | CHANGING ROOM 1 | Card reader |  |  | 1 |  | TBD |  |  |  |  | 24 | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1061 | CHANGING ROOM 1 | Door | Door to access Barrier area H09.100.1016 |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1062 | WC | WC |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1062 | WC | SINK |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1063 | SHOWER | SHOWER |  |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1063 | SHOWER | Floor drain | conected to conventional ww. |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1064 | SHOWER | SHOWER |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1064 | SHOWER | Floor drain | conected to conventional ww. |  |  |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1065 | WC | WC |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1065 | WC | SINK |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.100.1066 | CHANGING ROOM 2 | Lockers with benches | There shall be at least one locker a worker for storing personal items |  | 6 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1066 | CHANGING ROOM 2 | Card reader |  |  | 1 |  | TBD |  |  |  |  | 24 | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1066 | CHANGING ROOM 2 | Door | Door to access Barrier area H09.100.1016 |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1066 | CHANGING ROOM 2 | clothes hanging rack | Visitors do not need a locker, they will use a clothes hanging rack. This is also needed for outwear in case of snow or rain. |  | 4 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | SEC
H09.100.1067 | KITCHENETTE | Microwave oven |  |  | 1 | 100 | Not CF |  | 100 |  |  | 230 | 2 | 1 |  |  | N | N | N/A | ES&H
H09.100.1067 | KITCHENETTE | coffee machine |  |  | 1 | 100 | Not CF |  | 100 |  |  | 230 | 1.5 | 1.5 |  |  | N | N | N/A | ES&H
H09.100.1067 | KITCHENETTE | dishwasher |  |  | 1 | 500 | Not CF |  | 500 |  |  | 230 | 2 | 1 |  |  | N | N | N/A | ES&H
H09.100.1067 | KITCHENETTE | Floor drain | conected to conventional ww. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1068 | OPERATIONS CENTRE | Computers |  |  | 3 | 2000 | Not CF |  | 6000 |  |  | 230 | 10 | 5 |  |  | Y | Y | N/A | ES&H
H09.100.1068 | OPERATIONS CENTER | Desks |  |  | 2 | 100 | Not CF |  | 200 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1068 | OPERATIONS CENTER | chairs |  |  | 2 | 100 | Not CF |  | 200 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1068 | OPERATIONS CENTER | C&M Network, Data Outlet 2xRJ45 | For data transport to computers. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1068 | OPERATIONS CENTER | GPN Network, Data Outlet 2xRJ45 | For data transport to computers. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1068 | OPERATIONS CENTER | ICS Network, Data Outlet 2xRJ45 | For data transport to computers. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1068 | OPERATIONS CENTER | Card reader |  |  | 1 |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1068 | OPERATIONS CENTER | Door | Door to access control room |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1069 | OFFICE | Desks |  |  | 6 | 100 | Not CF |  | 600 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1069 | OFFICE | chairs |  |  | 6 | 100 | Not CF |  | 600 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1069 | OFFICE | Computers |  |  | 6 | 2000 | Not CF |  | 12000 |  |  | 230 | 10 | 5 |  |  | N | N | N/A | ES&H
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1069 | OFFICE | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.100.1070 | STAFF ROOM | chairs |  |  | 10 | 100 | Not CF |  | 1000 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1070 | STAFF ROOM | Kitchen & meeting table | for 10 people |  | 1 | 300 | Not CF |  | 300 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1070 | STAFF ROOM | Projector | One table + chairs for 13 people + projector etc. |  | 1 | 650 | Not CF |  | 650 |  |  | 230 | 1 | 0.5 |  |  | N | N | N/A | ES&H
H09.100.1070 | STAFF ROOM | Floor box | 4 pcs. 10 A 1 phase outlets |  | 1 |  | CF | CF |  |  |  | 230 | 5 | 1 |  |  | N | N | N/A | Electric
H09.100.1070 | STAFF ROOM | Whiteboard |  |  | 2 | 200 | Not CF |  | 400 |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.100.1070 | STAFF ROOM | EMERGENCY EXIT |  |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.100.1070 | STAFF ROOM | GPN Network, Data Outlet 2xRJ45 | For data transport to computers etc. |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1001 | STORAGE | EMERGENCY EXIT | Emergency exit to room H09.110.1002 |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1001 | STORAGE | Empty moulds etc. | 6T empty moulds 2T Empty barrels 4T empty modullådor |  | 12 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | 12000 | STRUCTURE
H09.110.1001 | STORAGE | Process cabinet |  |  | 1 |  | CF | cf |  |  |  | 400 | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.110.1001 | STORAGE | Electric equipment | Electric cabinet on the contcolled area servicing Process equipment |  | 1 | [6 empty] | 400 | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1001 | STORAGE | ICS Network, Data Outlet 2xRJ45 | For data access to Process cabinet |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1001 | STORAGE | C&M Network, Data Outlet 2xRJ45 | For data access to Process cabinet |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1001 | STORAGE | C&M Network, Data Outlet 2xRJ45 | For data access to Process cabinet |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1001 | STORAGE | GPN Network, Data Outlet 2xRJ45 | For data transport to Electric cabinet |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.110.1002 | CEMENTATION | Overhead/Telfer crane | This crane will be needed to move 2 ton cement and concrete sacks (Cone cranes) |  | 1 | 3900 | CF | 3900 |  |  |  | 400 | 2.75 | 2 |  |  | N | Y | 400 | TRANSPORT
H09.110.1002 | CEMENTATION | Solidification system | The system handling distribution of chemicals, water, etc. to the solidification process in the grouting room |  | 0 | 3000000 | Not CF |  | 0 |  |  | 400 | 10 | 5 |  |  | N | Y | 500 | ES&H
H09.110.1002 | CEMENTATION | Cementation and concrete handling equipment | Mixing of water and cement or concrete |  | 1 | included above | Not CF |  | ES&H |  |  | 400 | 10 | 5 |  |  | N | Y | 1000 | ES&H
H09.110.1002 | CEMENTATION | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.110.1002 | CEMENTATION | Dosimetry system | This is not a room on controlled area, but TLD and EPD are mandatory |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.1 | 0.1 |  |  | N | N | N/A | ES&H
H09.110.1002 | CEMENTATION | Chemical storage | Room for placing the chemicals needed for the grouting process. |  | TBD |  | Not CF |  | ES&H |  |  | 230 | 0.2 | 0.2 |  |  | N | Y | 14000 | ES&H
H09.110.1002 | CEMENTATION | System to enable monitoring the grouting | The workers handling the distribution in this room need to gain information of the status in the grouting room, this can be done via a TV-screen from camera |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.1 | 0.1 |  |  | N | Y | N/A | ES&H
H09.110.1002 | CEMENTATION | EMERGENCY EXIT | Emergency exit FROM room H09.110.1001 |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1002 | CEMENTATION | HVAC equipment | Extract fan | PAS01-EF001 | 1 | [6 empty] | 230 | 0.2 | 0.2 |  |  | N | N | N/A | HVAC
H09.110.1002 | CEMENTATION | Penetrations in intermediate floor | There shall be 3 DN200 penetrations through the intermediate floor between room H09.110.1002 and room H09.100.1001 | [8 empty] | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1002 | CEMENTATION | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.110.1002 | CEMENTATION | Magnetic switches | for door |  | 1 |  | CF | CF |  |  |  | 24 | N/A | N/A |  |  | Y | Y | N/A | Electric
H09.110.1002 | CEMENTATION | Door | Door for access from/to outside |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1002 | CEMENTATION | Floor drain | conected to basin outside |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1003 | PURFICATION ROOM L2 | Tap | with cold deionised water |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.110.1003 | PURFICATION ROOM L2 | Floor dran | For water from the tap |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.110.1003 | PURFICATION ROOM L2 | Hatch to room H09.100.1003 | In case mishaps in room H09.100.1003, high pressure washing using deionised water is needed. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1003 | PURFICATION ROOM L2 | Legal sampling station | Leagal sampling station for water to be sampled during release. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | PROCESS
H09.110.1003 | PURFICATION ROOM L2 | Reserved space for 10 T in the south end | Thins, not specified |  |  |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | 10000 | STRUCTURE
H09.110.1003 | PURFICATION ROOM L2 | Outlet box | 3 pcs. 16 A 1 phase outlets 1 pcs. 16 A 3 phase outlet 1 pcs. 32 A 3 phase outlet |  | 1 |  | CF | CF |  |  |  | 400 | 15 | 2 |  |  | N | N | N/A | Electric
H09.110.1003 | PURFICATION ROOM L2 | Hoses |  |  |  |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | 5000 | STRUCTURE
H09.110.1003 | PURFICATION ROOM L2 | Evaporator |  |  | 1 |  | CF |  |  |  |  | 400 | 32 | 30 |  |  | N | N | 2000 | PROCESS
H09.110.1003 | PURFICATION ROOM L2 | Water heater | Water heater for DIW |  | 1 |  | CF |  |  |  |  | TBD | TBD | TBD |  |  | N | N | 500 | PROCESS
H09.110.1004 | STAIR | [10 empty] | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1005 | STORAGE | [5 empty] | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.110.1006 | SHAFT | PIPE | HVAC PIPING |  |  |  | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.110.1007 | STORAGE |  |  |  | N/A |  | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.115.1000 | STAIR |  |  |  | N/A |  | Cf | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.115.1001 | UNCONTROLLED HVAC | HVAC equipment | AHU | AHS01-AHU001 | 1 |  | CF | CF |  |  |  | 400 | 2.4 | 2.4 |  |  | N | N | 370 | HVAC
H09.115.1001 | UNCONTROLLED HVAC | HVAC equipment | Heating, Shunt | AHS01-SS001 | 1 | [6 empty] | 230 | 0.1 | 0.1 |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | HVAC equipment | Cooling, shunt | AHS01-SS002 | 1 | [6 empty] | 230 | 0.2 | 0.2 |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | dampers |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | INLET Filters |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | Self closing isolating valves |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | Blast panels | In case of under pressure in the ventilation room, the blast panel opens and thereby secure the structural integrity of the room. |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.115.1001 | UNCONTROLLED HVAC | Control system connected to fire alarm |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | Sump or something similar | To stop RWW from flodding the room in case of sprinkler release |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | slop basin | For emptying liquid waste, this one is equiped with hot and cold domestic water and connected to RWW. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | Floor dran | connected to conventional ww. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1001 | UNCONTROLLED HVAC | C&M Network, Data Outlet 2xRJ45 | For data transport |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | AHU | PAS01-SAU001 | 1 |  | CF | CF |  |  |  | 400 | 11 | 11 |  |  | N | N | 1300 | HVAC
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | AHU | PAS02-EAU001 | 1 | [6 empty] | 400 | 4 | 4 |  |  | N | N | 660 | HVAC
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | AHU | PAS03-EAU001 | 1 | [6 empty] | 400 | 2.2 | 2.2 |  |  | N | N | 600 | HVAC
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | Heating, Shunt | PAS01-SS001 | 1 | [6 empty] | 230 | 0.5 | 0.5 |  |  | N | N | 100 | HVAC
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | Heating, Shunt | PAS01-SS002 | 1 | [6 empty] | 230 | 0.5 | 0.5 |  |  | N | N | 100 | HVAC
H09.115.1002 | CONTROLLED HVAC | HVAC equipment | Cooling, shunt | PAS01-SS003 | 1 | [6 empty] | 230 | 0.5 | 0.5 |  |  | N | N | 100 | HVAC
H09.115.1002 | CONTROLLED HVAC | dampers |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | HEPA Filters |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | Self closing isolating valves |  |  | TBD |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | Blast panels | In case of under pressure in the ventilation room, the blast panel opens and thereby secure the structural integrity of the room. |  | 2 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | STRUCTURE
H09.115.1002 | CONTROLLED HVAC | Control system connected to fire alarm |  |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | slop basin | For emptying liquid waste, this one is equiped with hot and cold deionised water and connected to RWW. |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | Gap under door | function to deal with the internal flooding in case of sprinkler release |  | 1 |  | CF |  |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1002 | CONTROLLED HVAC | Electric equipment | Electric cabinet on the contcolled area servicing HVAC equipment etc. |  | 1 | [6 empty] | 400 | N/A | N/A |  |  | N | N | N/A | Electric
H09.115.1002 | CONTROLLED HVAC | C&M Network, Data Outlet 2xRJ45 | For data transport to HVAC control system |  | 1 | [6 empty] | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.115.1003 | STACK MONITORING ROOM | System for detection of radionuclides | UPS secured, conected to REMS |  | 1 | 500000 | Not CF |  | ES&H |  |  | 230 | 1 | 1 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Flow rate monitoring equipment | UPS secured |  | 1 | see above | Not CF |  | ES&H |  |  | 230 | 0.5 | 0.1 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Piping, valves and fans for measuring loop(s) | This is needed for the environmental instrumentation in the ventilation stack monitoring room |  | 1 | see above | CF | CF |  |  |  | 230 | 1 | 1 |  |  | TBD | TBD | N/A | HVAC
H09.115.1003 | STACK MONITORING ROOM | Sampling line | UPS secured |  | 1 | see above | Not CF |  | ES&H |  |  | 230 | 1 | 1 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Iodine sampling station | UPS secured, conected to REMS (if possible) |  | 1 | see above | Not CF |  | ES&H |  |  | 230 | 1 | 1 |  |  | Y | Y | 150 | ES&H
H09.115.1003 | STACK MONITORING ROOM | filters |  |  | 1 | see above | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | aerosol filters |  |  | TBD | see above | Not CF |  | ES&H |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | System for measuring volume releases of exhaust air | UPS secured, conected to REMS |  | TBD | see above | Not CF |  | ES&H |  |  | 230 | 0.3 | 0.3 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Eye washer | The detection aprartus is expected to contain lye |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Air flow rate instrumentation | UPS secured, conected to REMS |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.3 | 0.3 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Thermometer | UPS secured |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.1 | 0.1 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Humidity measurement | UPS secured |  | 1 |  | Not CF |  | ES&H |  |  | 230 | 0.1 | 0.1 |  |  | Y | Y | N/A | ES&H
H09.115.1003 | STACK MONITORING ROOM | Gap under door | function to deal with the internal flooding in case of sprinkler release |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | HVAC
H09.115.1003 | STACK MONITORING ROOM | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
H09.115.1003 | STACK MONITORING ROOM | GPN Network, Data Outlet 2xRJ45 | For data transport |  | 1 |  | CF | CF |  |  |  | N/A | N/A | N/A |  |  | N | N | N/A | Electric
Note on L2: Michael: substation, switch, switchboard, outlet
Note on M2: Michael: Possibility to list phase
Note on C135: Elise: http://www.unionrope.com/Resource_/TechnicalReference/2418/Block%20rotation%20and%20rope%20stability-Cranes.pdf
Note on D257: Elise: see http://www.hydraulkraft.se
Note on T40: Tobias Hörnfeldt: Weight of Craine (with hoists)