## First Sheet
DM--SR-TBSIDDH01-System Requirements H01 CUB.xls
|  | Name | Role/Title
| Owner |  | Requirement engineer, CF
| Reviewer |  | Building Owner CF
| Approver |  | Baseline Team Lead
Review comments are found in ESS-0154142

## Requirement list
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Into NCR? | Status | Deviation To NCR? | User Defined ID | Verification Description | Comment
|  | Global warming potential of refrigirants | The GWP of refrigirants shall be <10. | 13933 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-1
|  | Man 1 Sustainable Procurement - Integrated design 1-2 | From design brief stage the client, building occupier, design team and contractor shall be involved in contributing to the decision making process for the project. As a minimum this includes meeting to identify and define their roles, responsibilities and contributions during the following phases: a. Design b. Construction c. Commissioning and handover d. Occupation, i.e. up to and including post practical completion stage The roles and responsibilities outlined above include consideration of: a. End user requirements b. Aims of the design and design strategy c. Particular installation and construction requirements d. Occupier's budget and technical expertise in maintaining any proposed systems e. Usability and manageability of any proposals f. Production of documentation g. Commissioning,training and aftercare support | 14297 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-2
|  | Databases for assessment of hazardous substances | Built in products shall be certified according to Byggvarubedömningen, Sunda Hus or BASTA and achieve one of the following criteria levels: Byggvarubedömningen - criteria level Accepted or Recommended Sunda Hus - criteria level A, B or C+ BASTA - registration in BASTA Byggvarubedömningen shall be used primarily. | 13881 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-3
|  | Halogenated materials | Materials shall be free of halogens (F, Cl, Br). | 13882 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-4
|  | Light emissions | The outdoor lightning shall be concentrated on the object to be illuminated by directing the light source correctly and by selecting lighting with proper design. Outdoor lighting shall not be directed to the surrounding residences and road-users. | 13877 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-5
|  | Extinguishing water collection | Extinguishing water shall be collected in a special tank system and as a final measure go with the storm water to the detention ponds. The ponds shall then be shut off for sampling, treatment or disposal. | 13867 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-6
|  | Collection systems for solid and liquid waste | SI shall be equipped with collection systems with seperate fractions for solid and liquid wastes. | 13868 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-7
|  | Effective circulation pumps | All circulation pumps shall have EEI 0.23 or better | EHS-NRG-004 | ESS-0078440/ ESS-0043151 | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-8
|  | Effective electrical motors | Electrical motors shall be of energy efficiency class IE4 or better according to SS-EN 60034-30-1 | EHS-NRG-008 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-9
|  | Effective Transformers | All transformer shall be at least as energy efficient as required by tier 2 in EU 548/2014 | EHS-NRG-010 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-10 |  | Not applicable in H09
|  | HV- and LV system power measurements | It shall be possible to perform continuous energy measurement on symmetric and asymmetric loads both on the HV- and LV systems. Error tolerance = 1,0% (MID Class B) | EHS-NRG-011 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-11 |  | Delete
|  | Primary Substation power measurements | It shall be possible to perform continuous energy measurement on symmetric and asymmetric loads on the Primary Substation (H05). Error tolerance = 0,2% (MID Class D) | EHS-NRG-012 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [13 empty] | Yes | SRH09-12 |  | Per Pihl, explain why it is not to be used in H09.
|  | Lightning power measurements | It shall be possible to measure electrical consumption of Lighting only, separated from all other electricity consumption | EHS-NRG-013 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-13 |  | Delete?
|  | Ventilation power measurements | It shall be possible to measure electrical consumption of Ventilation only, separated from all other electricity consumption | EHS-NRG-014 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-14
|  | Sub-metering of laboratory safety ventilation (air flow) | HVAC air extraction flows from laboratory safety ventilation shall be equipped with air extraction flow meters inside the duct system placed at the laboratory boarder (=close to the wall or roof) to verify total regulatory air flow from laboratory equipment | EHS-NRG-044 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-15
|  | Zinc in contact with water | Zinc in materials and products at ESS that are in contact with water and where there is a risk of release of this substance into the environment shall be replaced by other alternative materials. | EHS-SUS-002 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-16
|  | Copper in contact with water | Copper in materials and products at ESS that are in contact with water and where there is a risk of release of this substance into the environment shall be replaced by other alternative materials. | EHS-SUS-003 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-17
|  | Sulfur hexafluoride | Sulfur hexafluoride (SF6) shall not be used at ESS. | EHS-SUS-004 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-18
|  | TVOC emissions | Indoor surface treatment materials and products used at ESS shall not exceed TVOC emission levels described in EN 717-1:2004 or ISO 16000-9, depending on which method used for verification. | EHS-SUS-005 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-19
|  | ROHS | ESS shall conform to Directive 2002/95/EC on the restriction of the use of hazardous substances in electrical and electronic equipment (RoHS). | EHS-SUS-011 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-20
|  | REACH | ESS shall conform to Regulation (EC) No 1907/2006 concerning Registration, Evaluation, Authorisation and Restriction of Chemicals (REACH). | EHS-SUS-024 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-21
|  | Material selection | ESS shall not contain hazardous substances exceeding limits defined in www.bastaonline.se. | EHS-SUS-025 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-22
|  | Halogenated materials | Materials at ESS shall be free of halogens (F, Cl, Br) | EHS-SUS-026 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-23
|  | Environmental court verdict | Chemical products shall be handled in a way that spills and leaks can not reach sewers or the environment | EHS-SUS-033 |  | ESS-0078440/ ESS-0043151 ESS-0031401 | [14 empty] | SRH09-24
|  | Environmental court verdict | Hazardous waste shall be handled in a way that spills and leaks can not reach sewers or the environment | EHS-SUS-038 |  | ESS-0078440/ ESS-0043151 ESS-0031402 | [14 empty] | SRH09-25
|  | Environmental court verdict | Storage of Chemical products shall take place on a surface that is impermeable for the products stored | EHS-SUS-043 |  | ESS-0078440/ ESS-0043151 ESS-0031403 | [14 empty] | SRH09-26
|  | Environmental court verdict | Storage of chemical products shall be fitted with bunding or similar to protect against leaks | EHS-SUS-048 |  | ESS-0078440/ ESS-0043151 ESS-0031404 | [14 empty] | SRH09-27
|  | Environmental court verdict | Storage of chemical products shall be otherwise designed so that precipitation does not accumulate in it | EHS-SUS-053 |  | ESS-0078440/ ESS-0043151 ESS-0031405 | [14 empty] | SRH09-28
|  | Environmental court verdict | The volyme of the bunding to collect spill in the chemical storage shall correspond to the volyme of the largest container in the storage plus 10% of the total volyme of the other stored chemical containers | EHS-SUS-058 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | [14 empty] | SRH09-29
|  | Environmental court verdict | Storage of hazardous waste shall take place on a surface that is impermeable for the waste stored | EHS-SUS-063 |  | ESS-0078440/ ESS-0043151 ESS-0031407 | [14 empty] | SRH09-30
|  | Environmental court verdict | Storage of hazardous watse shall be fitted with bunding or similar to protect against leaks | EHS-SUS-068 |  | ESS-0078440/ ESS-0043151 ESS-0031408 | [14 empty] | SRH09-31
|  | Environmental court verdict | Storage of hazardous waste shall be otherwise designed so that precipitation does not accumulate in it | EHS-SUS-073 |  | ESS-0078440/ ESS-0043151 ESS-0031409 | [14 empty] | SRH09-32
|  | Environmental court verdict | The volyme of the bunding to collect spill in the hazardous waste storage shall correspond to the volyme of the largest container in the storage plus 10% of the total volyme of the other stored chemical containers | EHS-SUS-078 |  | ESS-0078440/ ESS-0043151 ESS-0031410 | [14 empty] | SRH09-33
|  | Environmental court verdict | Storage tanks shall be equipped with overfill protection | EHS-SUS-083 |  | ESS-0078440/ ESS-0043151 ESS-0031411 | [14 empty] | SRH09-34
|  | Environmental court verdict | Absorbent shall be available at chemical storages | EHS-SUS-088 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-35
|  | Environmental court verdict | Absorbent shall be available at hazardous waste storages | EHS-SUS-093 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-36
|  | Volume of wastewater from laboratories | Waste water from laboratories shall be minimized and collected locally for monitoring of contamination level prior to discharge to the municipal sewage system. | 13842 |  | ESS-0031412 | [14 empty] | SRH09-37
|  | Chemical waste | Chemical waste from laboratories shall be stored adjacent to where it was generated, awaiting disposal. | 13844 |  | ESS-0031412 | [14 empty] | SRH09-38
|  | Environmental court verdict noise operation | Noise from ESS operations, including transports within the ESS site, can not cause an equivalent noice level outdoors at residential areas exceeding 50 dB (A) at day time, business days Monday to Friday (07-18) 40 dB (A) at night, (22-07) 45 dB (A) other times | EHS-SUS-103 |  | ESS-0078440/ ESS-0043151 ESS-0031411 | [14 empty] | SRH09-39
|  | Environmental court verdict noise during the night | Operations that typically can momentarily exceed noice levels of 55 dB (A) can not be carried out during the night (22-07) | EHS-SUS-109 |  | CF sustain req ESS-0031401 ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-40
|  | Environmental court verdict noise operation | Noice from ESS operations can not cause an equivalent noice level outdoors at working premises exceeding 60 dB (A) at day time, Monday to Friday (07-18) 50 dB (A) at night, (22-07) 55 dB (A) other times | EHS-SUS-115 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-41
|  | Environmental court verdict approve sewage effluents | Diverted effluents to the municipal sewage system has to be approved in advance by the municipality and by the supervicory authorities according to the Swedish environmental code | EHS-SUS-122 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-42
|  | Environmental court verdict separate sewage | The sewage system for sanitary sewage and other sewage water shall be separated | EHS-SUS-127 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-43
|  | Environmental court verdict close flow to municipas sewage | It shall be possible to close the flow to the municipal sewage system. | EHS-SUS-132 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-44
|  | Environmental court verdict collect sewage | Sewage, where discharge is prohibited, shall be collected and handled as waste | EHS-SUS-133 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-45
|  | Monitoring of contamination level | The volume of wastewater from laboratories shall be minimized and collected locally for monitoring of contamination level prior to discharge to the municipal sewage system. | 13851 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-46
|  | Laboratories design | Laboratories shall be designed so as to prevent hazardous substances from ending up in the wastewater. | 13852 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-47
|  | Floor drains | Floor drains shall be connected to separate tanks if drains are needed in potentially (radioactive) contaminated areas. | 13853 |  | CF sustain req ESS-0031401 | [14 empty] | SRH09-48
|  | Lightning Protection | All ESS facilities shall be protected by Lightning Protection Level LPS II (2) in standard SS-EN 62305-3, or better | EHS-ELC-001 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-49 |  | Delete?
|  | Hazardous voltage | All touchable metallic construction parts (e.g. between electrical cubicles and metallic fences or between electrical instruments and other metallic constructions such as pipes, cable ladders and ventilation ducts), shall be grounded so that people in the facilities will not come in contact with hazardous voltage (more than 50 V), based on measured resistance for all touchable metallic construction parts in ratio to "grounding" shall whitstand dimensioned and actual fault short circuit current of 24 kA, 1 sec (design 20 kA x 120 %=24 kA) and 50 kA (peak) from the electrical grid or actual fault short circuit current from other electrical equipment. | EHS-ELC-007 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-50 |  | Delete?
|  | Short circuit resistance | All metallic parts which are part of the grounding system (e.g. iron bars, main ring conductors) shall whitstand dimensioned and actual fault short circuit current of 24 kA, 1 sec (design 20 kA x 120 %=24 kA) and 50 kA (peak) from the electrical grid or actual fault short circuit current from other electrical equipment. Note that the metallic parts shall withstand both thermical and mechanical forces from the fault short circuit current. | EHS-ELC-013 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-51 |  | Delete?
|  | Grounding standard | Grounding shall comply with grounding system TN-S | EHS-ELC-019 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-52 |  | Delete?
|  | Arc guard protection cubilces | Each cubicle used in the power distribution system shall be equipped with an arc guard system that monitors and detects arc opticals. | EHS-ELC-033 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-53 |  | No cubicles are installed in H09
|  | Arc guard protection switchgears | Power supply to switchgears in the power distribuion system shall be disconected if an optical arc is detected by the arc guard system. | EHS-ELC-034 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-54 |  | No switchgears in H09
|  | Fixed grounding switches | Transformers and cubicles shall be equipped with fixed grounding switches (compliant with EN 62271-102) on the HV- and LV systems | EHS-ELC-043 |  | ESS-0078440/ ESS-0043151 | [13 empty] | Yes | SRH09-55 |  | Per Pihl, förklara varför det ej gäller i H09
|  | Locks and tags | Transformers and cubicles shall be equipped with locks and tags on the HV- and LV systems | EHS-ELC-044 |  | ESS-0078440/ ESS-0043151 | [13 empty] | Yes | SRH09-56 |  | Per Pihl, förklara varför det ej gäller i H09
|  | Isolate electrical main suppliers | It shall be possible to isolate electrical main suppliers from each other on the HV- and LV side | EHS-ELC-045 |  | ESS-0078440/ ESS-0043151 | [13 empty] | Yes | SRH09-57 |  | Per Pihl, förklara varför det ej gäller i H09
|  | Overvoltage protection | An overvoltage protection system shall be implemented on LV- and HV systems. (According to SS-EN 61643-11) | EHS-ELC-046 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-58 |  | Delete?
|  | Earth Fault Monitoring LV switchboard | It shall be possible to detect and measure earth faults on the LV switchboard systems with a preinstalled earth fault monitoring system. | EHS-ELC-048 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-59 |  | No LV switchboard systems in H09
|  | Earth Fault Monitoring alarm SCADA | If the earth fault monitoring system detects an error, an alarm should also be sent to the SCADA system. | EHS-ELC-049 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-60 |  | Per Pihl, förklara vad det är som inte finns i H09
|  | Earth Fault Monitoring presented locally | Errors originating from the earth fault monitoring system shall be presented locally at the switchboard. | EHS-ELC-050 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-61 |  | No switchboard systems in H09
|  | Emergency shut down button | An emergency shutdown button shall be installed next to each switchboard entrace door. | EHS-ELC-051 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-62 |  | No switchboard systems in H09
|  | Emergency shut down switchboard | The switchboard emergency shutdown button shall, if pressed, shut down the power to the switchboard from overlaying and underlaying network circuits. | EHS-ELC-052 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-63 |  | No switchboard systems in H09
|  | LV Ampere measurements | It shall be possible to measure thermal lag of 15 minutes, max ampere values and real time current. The data shall be presented at the switchgear with an indicating instrument, even in case of a power failure. This applies per phase at each incoming LV power supply cubicle, before the circuit breaker. | EHS-ELC-055 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-64 |  | No switchgears in H09
|  | LV Voltage measurements | LV systems shall be equipped with a V-meter, and connected changeover switch, that monitor voltage between the different phases at each incoming LV power supply cubicle before the circuit breaker | EHS-ELC-056 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-65 |  | No switchgears in H09
|  | Electrical installations | Electrical installations shall comply to SS-EN-ISO | EHS-FIR-001 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-66 |  | Delete?
|  | Cable installations | Cables shall be fire retardant and non corrosive in compliance with ESS-0034035 | EHS-FIR-011 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-67 |  | Delete?
|  | Access to portable extinguishers | Indoor Distance to nearest portable extinguisher or fire hose shall be maximum 25 m | EHS-FIR-020 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-68
|  | Fire Water Supply Capacity | The fire water supply shall meet the capacity requirements in ESS-0002642 Ch 2.2. | EHS-FIR-021 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-69
|  | Fire Water Freezing resistance | The fire water supply shall meet the water freezing requirements in ESS-0002642 Ch 2.2 (E.g. distribution line depth of 1,9 m for gravel and sand soil). | EHS-FIR-022 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-70
|  | Fire Water Seismic resistance | The fire water supply shall meet the seismic requirements in ESS-0002642 Ch 2.2. | EHS-FIR-023 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-71
|  | Heater | Heat sources in ventilation systems shall be constructed so that they cannot cause fires in filters, which means that electrical heaters and other possible ignition sources must not be used in air handling units | EHS-FIR-026 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-72
|  | Exposed combustibles | Combustible materials shall be protected as specified by ESS-0002381 (If nothing is specified, protective cladding shall meet A2-s1,d0) | EHS-FIR-027 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-73
|  | Planning and Building Act | Fires shall be prevented from starting by applying requirements in ESS-0002381 | EHS-FIR-039 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-74
|  | Detection coverage | Automatic fire alarm shall cover all areas of the facility in compliance with SBF 110:7 110:6 | EHS-FIR-045 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-75
|  | Fire alarm to SOS | The fire alarm shall be directly connected to the municipal SOS alarm center | EHS-FIR-046 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-76
|  | Emergency Response Team | Fire alarm equipment shall be connected to SOS with an alarm storage delay of 3 to 5 minutes | EHS-FIR-047 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-77
|  | Radiation resistant detectors | Fire detection equipment shall retain its performance for minimum 2 years in areas exposed to ionization radiation | EHS-FIR-050 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-78
|  | Automatic Water Suppression - ESS-0002381 | Automatic suppression system shall be installed as required by the planning and building act in ESS-0002381 | EHS-FIR-058 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-79
|  | Automatic Water Suppression - sprinkler standard | Automatic suppression system shall be installed as required by the sprinkler standard SS/EN 12845:20 04+A2:2009 | EHS-FIR-059 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-80
|  | Automatic Water Suppression - ESS-0002642 | Automatic suppression system shall be installed wherever manual fire fighting can not be achieved ref ESS-0002642 | EHS-FIR-060 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-81
|  | General lighting - access route | Indoor access route general lighting strength shall be minimum 100 lux | EHS-FIR-067 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-82
|  | General lighting - separate circuits | Every other source of general lighting in access routes shall be powered by separate circuits (fuses). fuse-boxes and earth to ground breakers. | EHS-FIR-068 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-83
|  | Ventilation at basic point | Staircase at Point of Access/Basic point shall be smoke ventilated with hatch or overpressure with fan to ensure efficient entrance for fire brigade if staircase exceeds two floor levels | EHS-FIR-069 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-84
|  | Limit pool size | Transformer pits shall contain insulation liquid + fire suppression agent as defined ref ESS-0002642 Ch 5.3 | EHS-FIR-071 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-85
|  | Flooding - contain residual water | SI buildings shall have the capacity to contain residual fire water as defined by ESS-0004481 | EHS-FIR-072 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-86
|  | Flooding - electrical cabinet | None SSC - electrical cabinets shall have a drain hole in the bottom and be placed on a pedestal high enough to keep the electronics above the drainage curbing of the specific area and to allow any water that gets inside the cabinet to drain. (only desirable according to CF) | EHS-FIR-087 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-87
|  | Flooding - electrical equipment IPX2 | None SSC electrical equipment shall comply with IPX2 in sprinkler areas | EHS-FIR-093 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-88
|  | Flooding - sprinkler head | Closed head sprinkler shall have metal fuse link nozzle (not glass bulb) | EHS-FIR-099 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-89
|  | Flooding - sprinkler pipes seismic qualified | Sprinkler pipes shall be seismic qualified in areas passing SSC- electrical equipment | EHS-FIR-100 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-90
|  | Insulation and grounding | Switches and breakers shall be installed and easily identified for quick and remote insulation and grounding of potentials at AC 1000 V, DC 1500 V (or higher) according to EPIP see EHS-FIR-100 | EHS-FIR-102 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-91
|  | Smoke management | Hatches for evacuation of smoke shall be installed as required by the ESS-0002381 | EHS-FIR-113 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-92
|  | Fire rated barrier distance between buildings | Buildings of different building classifications shall be separated by an outdoor distance of 8 m or firewall in alignment to BBR20 table 5.562 | EHS-FIR-114 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-93
|  | Fire rated barrier H09 | The boundary walls separating H09 Waste Building from any other building shall function as fire walls in accordance to BBR20 table 5.562 or equal. | EHS-FIR-115 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-94
|  | Fire rated barrier compartmentalizations | Fire compartmentalization shall be established as required by the planning and building & flammable and explosives act ref ESS-0002381 | EHS-FIR-122 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-95
|  | Fire rated barrier separation of power train C1 | Separation of redundant power train (SaF C1 = Safety Function Category 1) shall be minimum REI 60 | EHS-FIR-123 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-96
|  | Fire rated barrier separation of power train C2 | Separation of redundant power train (SaF C2 = Safety Function Category 2) shall be minimum REI 60 | EHS-FIR-129 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-97
|  | Exhaust filters controlled areas | Filter banks shall be protected as defined by ESS-0002642 Ch 4.3 (automatic fire damper, water spray system inside the carbon filter with manual hose connection and automatic water suppression of the fire compartment) | EHS-FIR-156 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-98
|  | Automatic Water Suppression | Rooms with glove box or fume hood in controlled areas shall be protected with automatic water suppression or fire compartmentalized. | EHS-FIR-158 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-99
|  | Sewage | Sewage systems in controlled areas shut off mechanisms shall meet requirements on single failure and common cause failure in order to avoid risk of contamination outside perimeter | EHS-FIR-162 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-100
|  | Fire compartment | Each cable culvert shall form a separate fire compartment | EHS-FIR-165 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-101
|  | Automatic Water Suppression | Automatic water suppression shall be installed in all cable culverts, where fire cannot quickly get extinguished by other means | EHS-FIR-166 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-102
|  | Protection | Transformers shall be protected as defined in ESS-0002642 Ch 5.3 | EHS-FIR-169 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-103
|  | Cable installations | The general design rule for the facility is that cables shall not be spliced | EHS-FIR-173 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-104
|  | Outdoor combustibles | Outdoor recycling containers shall be kept minimum six (6) m from any building construction | EHS-FIR-180 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-105
|  | SSC vertical distance | A minimum separation distance of 30cm horizontal and 80cm vertical shall be applied to field equipment classified as SaF C1 and/or SaF C2 | EHS-FIR-185 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-106
|  | SSC horizontal distance | A minimum separation distance of 30cm horizontal anda 80cm vertical shall separate SaF and non-SaF equipment | EHS-FIR-186 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-107
|  | Engineering design | All facilities shall be designed to avoid formation of explosive athmospheres, in order to avoid explosion hazards. Possible design strategies include 1) choice of non flammables OR 2) flammables kept with 75% margin to Lower Explosion Limit or Fire point OR 3) inert atmosphere AND/OR 4) get in compliance with the explosions requirements EHS-EXP-XXX | EHS-EXP-005 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-108
|  | Engineering alignment standard | Explosion hazards shall be reduced by design in alignment with ISO-CEN-SIS standards. | EHS-EXP-011 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-109
|  | Ventilation flammables | Rooms where flammables are stored shall be ventilated. | EHS-EXP-017 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-110
|  | Ventilation flammables supervised by automatic system | The active mechanical ventilation in rooms where flammables are stored shall be supervised by an automatic system. | EHS-EXP-019 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-111
|  | Ventilation alarm | The automatic system that supervises the active mechanical ventilation shall trigger an alarm when any disruption occurs | EHS-EXP-020 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-112
|  | Ventilation cupboards interlock | The power supply of cupboards shall interlock when the mechanical ventilation fails | EHS-EXP-025 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-113
|  | Ventilation flammables negative pressure | Storage or handling of flammables shall have a negative pressure cascade in relation to adjacent room in normal operation | EHS-EXP-027 | ESS-0078440/ ESS-0043151 | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-114
|  | Ventilation flammables openings | The ventilation openings from rooms where flammables are stored shall terminate outdoors directly | EHS-EXP-028 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-115
|  | Ventilation distance air intake | The distance between ventilation exhaust from rooms where flammables are stored, and air intake shall be a minimum of 6 m | EHS-EXP-029 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-116
|  | Storage flammables | Flammables must only be stored in guarded areas | EHS-EXP-040 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-117
|  | Storage flammables access control | Flammables must only be stored in areas where valves and other regulating devices are under access contol in order to avoid unauthorized tampering | EHS-EXP-046 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-118
|  | Storage flammables protected from corrosion | Cylinders and containers with flammables shall be protected from corrosion (i.e. protected from rain and other corrosive aggressors) | EHS-EXP-048 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-119
|  | Storage flammables mechanical impact | Cylinders and containers with flammables shall be protected from mechanical impact from vehicles | EHS-EXP-049 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-120
|  | Storage flammables not with other fire load | Flammables shall not be stored together with oxidizers, toxic substance and other fire load. | EHS-EXP-050 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-121
|  | Program flammable liquids | Handling of flammable liquids shall be in compliance with SÄIFS2000:2, SRVFS2005:10, MSBFS2014:5, MSBFS2014:1 (aerosols), | EHS-EXP-067 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-122
|  | Program flammable gas | Handling of flammable gas shall be in compliance with SÄIFS1998:7 & SÄIFS2004:4 & SÄIFS1998:7 | EHS-EXP-073 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-123
|  | Program comply with act | Handling of flammable gas and liquids shall be in compliance with Flammable and Explosive Act SFS2010:1011 & the ordinance SFS2010:1075 & the regulation SRVF 2004:7, MSBFS2010:4, SÄIFS 1994:5, AFS1995:5, AFS2003:3, MSBFS2013:3 | EHS-EXP-079 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-124
|  | Storage compressed gas | Compressed flammable gas storage shall be separated by fire partitioning EI30 for 250 liters, EI60 for 250 liters, separate storage min 8 m from buildings 1000 liters | EHS-EXP-081 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-125
|  | Storage flammable liquids | Flammable liquids storage shall be protected from activities in other areas by fire rated partitioning, minimum table 15 & 16 & 21 in Ch 6.5.1 SÄIFS2000:2 | EHS-EXP-082 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-126
|  | Storage and piping considered in design | Provisions to confine emissions due to ruptures shall be considered by design, accidental leakage shall not spread through fire rated partitioning. | EHS-EXP-083 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-127
|  | Storage and piping | Provisions to confine emissions due to ruptures shall be considered by design, curbing shall be designed to meet conditions in SÄIFS2000:2 Ch 6.2, Ch 8 | EHS-EXP-084 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-128
|  | Hazard zoning establish | Hazard zoning shall be established in areas with potential explosive atmospheres, as defined by the 1999/92/EC, Article 7 and the explosion protection document | EHS-EXP-089 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-129
|  | Hazard zoning restriction | The hazard zoning areas shall be restricted to usage of equipment and protective systems in alignment of Directive 94/9/EG. Explosive qualified electrical equipment shall comply with SS-EN 60079-14, SS-EN 60079-17 | EHS-EXP-095 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-130
|  | Hazard zoning warning sign | Hazard zoning areas shall be provided with warning sign SRVFS2004:7 | EHS-EXP-101 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-131
|  | Gorunding laboratory areas | Laboratory areas with unconfined handling of flammable substances shall have semiconducting carpet or similar protection design SS4210822 | EHS-EXP-107 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-132
|  | Grounding Hazardous areas | All installations in HAZARDOUS AREAS shall have potential equalization | EHS-EXP-113 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-133
|  | Grounding exposed parts | EXPOSED PARTS shall be connected to the equipotential bonding system | EHS-EXP-119 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-134
|  | Grounding extraneous conductive parts | Extraneous conductive parts shall be connected to the equipotential bonding system | EHS-EXP-125 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-135
|  | Grounding earthing point | The potential equalization system of a HAZARDOUS AREA shall include at least one earthing point of all armour and screens of cables in the HAZARDOUS AREA, even if the earthing points are situated outside of the HAZARDOUS AREA | EHS-EXP-131 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-136
|  | Indoor handling flammable gas | Compressed flammable gas for daily handling shall be stored after usage, in a cabinet qualified for storage of pressurised gas cylinders | EHS-EXP-149 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-137
|  | Indoor handling pressurised gas | A cabinet qualified for storage of pressurised gas cylinders shall be available where areas for daily handling will occur | EHS-EXP-155 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-138
|  | Fume cupboard | Fume cupboards shall fulfil safety performance requirement given by SS-EN 14175-2 | EHS-EXP-161 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-139
|  | Reactive substance | Reactive substances and oxidizers shall be handled as required by SÄIFS 1999:2, SÄIFS 1996:4, SÄIFS 1995:6, SÄIFS 1989:5 | EHS-EXP-167 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-140
|  | Channel force from explosion | Systems and buildings shall by design channel the force from any high risk explosion area for protection of the personnel and SSC as determined by the analyses in the Fire & Explosion Safety Program ESS-0004390 | EHS-EXP-173 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-141
|  | SSC robustness analysis H3 explosion | Explosion shall be analysed as an initiating event in category "H3" | EHS-EXP-185 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-142
|  | SSC robustness analysis secondary explosion | Consequences from flammable cloud explosions ignited remote from the accidental release shall be considered, even if it is the secondary explosion | EHS-EXP-191 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-143
|  | Heat | SSC shall be protected from resulting jetflame within 2 m from point of accidental release. The distance is based on 1,2 m jetflame from a hydrogen cylinder and has to be adjusted for other sources. | EHS-EXP-197 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-144
|  | Missiles | SSC shall be protected from resulting missiles within 300 m from pressurized cylinders. The distance is based on acetylene or hydrogen cylinder which results in 8,6 kPa. A not reinforced concrete slab is sufficient protection (13,8 kPa). The protective measures has to be adjusted for other sources. | EHS-EXP-203 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-145
|  | Blast wave | SSC shall be protected from resulting side on pressure effects within 41 m from a pressurized cylinder. The distance is based on a hydrogen cylinder results in 2,76 kPa and slight disortion of steel frame builidng and has to be adjusted for other sources. | EHS-EXP-210 |  | ESS-0078440/ ESS-0043151 | [14 empty] | SRH09-146
|  | Perimeter in general | All buildings located within the guarded Campus area shall have an outer perimeter protection in line with SSF 200 protection class 2 and corresponding levels for lock in SS-EN 1627:2011 and SS-EN 3522. (The standard stipulates lock class 3 but we will supply locks with class 2.) | EHS-SEC-005 |  | ESS-0066475 | [14 empty] | SRH09-147
|  | Intruder alarm | SSF 130, SSF 140 and SSF 114 standards shall be applied to all intruder alarm installations | EHS-SEC-007 |  | ESS-0066475 | [14 empty] | SRH09-148
|  | Document CCTV | CF shall document the intended function of each camera in the CCTV surveillance system in accordance with the standards SSF1060:2, SS-EN 50132-1:1 and SS-EN 50132-7:2. | EHS-SEC-008 |  | ESS-0066475 | [14 empty] | SRH09-149
|  | Protected area | All passages such as gates, doors, culverts etc. into protected areas shall be connected to an intruder alarm. | EHS-SEC-009 |  | ESS-0066475 | [14 empty] | SRH09-150
|  | Alarm to SMR | All alarms triggered by security systems for physical protection shall be transmitted to the Security Monitor room | EHS-SEC-011 |  | ESS-0066475 | [14 empty] | SRH09-151
|  | Fire alarm to SMR | All fire alarms shall be transmitted to the Security Monitor room | EHS-SEC-012 |  | ESS-0066475 | [14 empty] | SRH09-152
|  | Fire alarm to MCR | All fire alarms shall be transmitted into the Main Control room | EHS-SEC-021 |  | ESS-0066475 | [14 empty] | SRH09-153
|  | Protected area CCTV | All entrances in to protected area shall be monitored by CCTV. (Entrances in to protected area will be monitored by CCTV accordimg to the physical security agreement.) | EHS-SEC-105 |  | ESS-0066475 | [14 empty] | SRH09-154
|  | Protected area lock | All passages such as gates, doors, culverts etc. through outer surrounding physical perimeter into protected area shall, as a minimum, be locked according to SS-EN 1627:2011 and SS-EN 3522, corresponding to SSF 200, protection class 2. (The standard stipulates lock class 3 but we will supply locks with class 2.) | EHS-SEC-106 |  | ESS-0066475 | [14 empty] | SRH09-155
|  | Protected area identification | All persons shall at each time when entering in to protected area be identified as an individual to ensure that the right person is given access to the protected area. (Only via card readers and CCTV) | EHS-SEC-107 |  | ESS-0066475 | [14 empty] | SRH09-156
|  | Protected area access control | All physical entrances in to a protected area by an individual shall be registered in ESS access control system. (Only via card readers and CCTV) | EHS-SEC-108 |  | ESS-0066475 | [14 empty] | SRH09-157
|  | Protected area intruder alarm | For all passages such as gates, doors, culverts etc. into proteced areas, an intruder alarm shall be installed. | EHS-SEC-109 |  | ESS-0066475 | [14 empty] | SRH09-158
|  | Protected area detection by CCTV | Intrusion in to protected area shall be able to be detected and verified immediately through CCTV. | EHS-SEC-110 |  | ESS-0066475 | [14 empty] | SRH09-159
Note on A1: Unique identifier
Note on B1: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on F1: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on K1: Name of the last reviewer
Note on L1: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on M1: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N1: The expected minimum value for the parameter of interest
Note on O1: The expected nominal value for the parameter of interest
Note on P1: The expected maximum value for the parameter of interest
Note on Q1: S.I. units for the value of interest specification.
Note on R1: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on T1: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on V1: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on W1: Text describing how this requirement shall be verified. Details of how and at when verification activities should be performed. Can be a CHESS reference to Verification Plan.
Note on S1: Tobias Hörnfeldt: Is this requirement a deviation from the original requirement that should be listed in the NCR?
Note on U1: Tobias Hörnfeldt: Is this requirement not appliked, if so.: Yes + Explain in comment