## DOORS Req. format
Object Identifier | Category | Discipline | Serial no. | Room no. | New Room No. | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Architectual reviewer | Result of review (A) | Structural reviewer | Result of review (S) | Residual Item | CFIL/ CFRFI | Comments
Fire
|  |  | R1 |  |  | Fire Means of egress | H09 shall conform with description in Fire Safety Strategy ESS-0002381 regarding means of egress. |  |  | ESS-0002381 | Analysis | Essential | [11 empty] | Fire consultant shall review drawings and confirm conformity in written statement. PD: After PD drawings are finished. DD: Update of statement after DD drawings are finshed. | Lars | Satisfactory | Andreas | N/A | NO
|  |  | R2 |  |  | Fire classified materials | H09 shall conform with the description in Fire Safety Strategy ESS-0002381 regarding materials . |  |  | ESS-0002382 | Analysis | Essential | [11 empty] | Fire consultant shall review drawings and confirm conformity in written statement. PD: After PD drawings are finished. DD: Update of statement after DD drawings are finshed. | Lars | Not Answered | Andreas | Satisfactory | YES |  | Compartments need to be reviewed during DD
|  |  | R3 |  |  | Fire Compartment | H09 shall conform with description in Fire Safety Strategy ESS-0002381 regarding fire compartments Björn Yndemark shall update ESS-0002381 during PD. Fire compartments shall be shown in the A-drawings. |  |  | ESS-0002381 | Analysis | Essential | [11 empty] | Fire consultant shall review drawings and confirm conformity in written statement. PD: After PD drawings are finished. DD: Update of statement after DD drawings are finshed. | Lars | Satisfactory | Andreas | Satisfactory | NO
|  |  | R4 |  |  | Fire structural resistance | H09 shall conform with description in Fire Safety Strategy ESS-0002381 regarding structural fire resistance. |  |  | ESS-0002381 |  | Essential | [11 empty] | Fire consultant shall review drawings and confirm conformity in written statement. PD: After PD drawings are finished. DD: Update of statement after DD drawings are finshed. | Lars | N/A | Andreas | Satisfactory | NO |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R5 |  |  | Smoke evacuation | H09 smoke evacuation shall be designed according to ESS (Björn Yndermark) - There is no need for separate smoke evacuation in this building. - Smoke will be evacuated through the gates |  |  | ESS-0007143 | Inspection | Essential | [11 empty] | PD and DD: Review drawings. Construction: inspection. | Lars | Satisfactory | Andreas | N/A | NO | CFIL-194 | See meeting 2017-08-16 found on confluence A&S
|  |  | R6 |  |  | Fire and explosion safety program shall be applied | The “Fire and Explosion Safety Program” [ESS-0004722] is applied for prevention of damages resulting from fire or explosion as an initiating event. The basis is to apply the defence in depth approach i.e. FIRE (fire resulting from antagonistic attack is excluded from the program) point 1-3 and Explosion point 4-6 - Fire will be covered by updates in ESS-0002381 - Explosion safety will be handled in the HVAC system description: -- Ventilation of fork lift charging station. - Explosion safety will be handled by Waste management by the use of administrative procedures. |  |  | BLA P 30 |  | Essential | [12 empty] | Lars | Not Answered | Andreas | N/A | YES |  | SEC: Have explosion hatches been considered when choosing wall material? Tobias: This should probabbly be taken into consideration first in DD. See meeting 2017-08-16 found on confluence A&S
|  |  | R7 |  |  | Evacuation routes | Evacuation routes to leave the building is arranged and equipped in alignment to the Fire Strategy Report (BR01DT-TBSIGDPS--Fire Safety Strategy Report.pdf (ESS-0002381 rev. 11)). - Evacuation from staff room shall be added to the layout. - Evacuation from above grouting room to grout distribution room shall be added to the layout. | ESS-0002381 | Architecture | BLA P 20 | Analysis | Essential | [12 empty] | Lars | Satisfactory | Andreas | N/A | NO |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R8 |  |  | Fire and explosion safety program point 2 | Detect and extinguish quickly those fires that do start o Special remark for the waste building. At the workshop with the municipal rescue service [ESS-0044371], it was made clear, that it cannot be expected from rescue leader to decide on indoor intervention in the waste building. Credible extinguishing efforts are from outside only. Hence there is a need for full cover automatic extinguishing system. o The sprinkler central room shall be a seperate room and follow the design in the sprinkler central room in E03, this is 3x2,5 m accordingly requirement 11387. o The sprinkler system shall cover as well controlled as uncontrolled area of H09, including the sprinkler central room. |  |  | BLA P 30 & “Fire and Explosion Safety Program” [ESS-0004722] |  | Essential | [12 empty] | Viggo | N/A | Andreas | N/A |  |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R9 |  |  | Fire and explosion safety program point 3 | Prevent the spread of those fires which have not been extinguished o Special remark for the waste building. The building will not have fire rated, openings to the atmosphere, hence the full cover automatic fire extinguishing system is made robust and reliable to compensate for this deficiency. If required from a radiological point of view, the system is designed to handle defence in depth level 3 [ESS-0001188 Chapter 4 Condition B3]. o There is no need for a specific classification plan for H09 |  |  | BLA P 30 & “Fire and Explosion Safety Program” [ESS-0004722] |  | Essential | [12 empty] | Viggo | N/A | Andreas | N/A |  |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R10 |  |  | Fire and explosion safety program point 5 | Minimize the risk of an explosion, if an explosive atmosphere cannot be avoided o This is done by HVAC installation on forklift charging station. |  |  | BLA P 30 & “Fire and Explosion Safety Program” [ESS-0004722] |  | Essential | [12 empty] | Viggo | N/A | Andreas | N/A |  |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R11 |  |  | Fire and explosion safety program point 6 | Implement design provisions necessary to limit the consequences of an explosion. o This is done by HVAC installation and administrative procedures. |  |  | BLA P 30 & “Fire and Explosion Safety Program” [ESS-0004722] |  | Essential | [12 empty] | Viggo | N/A | Andreas | N/A |  |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R12 |  |  | Fire and explosion safety program point 4 | Prevent explosions from occurring o This is done by HVAC installation and administrative procedures. |  |  | BLA P 30 & “Fire and Explosion Safety Program” [ESS-0004722] |  | Essential | [12 empty] | Viggo | N/A | Andreas | N/A |  |  | See meeting 2017-08-16 found on confluence A&S
|  |  | R13 |  |  | Br2 structure compliance | The load bearing structure shall have a robust design to stay in compliance with a Br2 structure over the entire lifetime of the building. Hence main loadbearing structures are protected from fire by solid passive fire rating. The source of this requirement is found in ESS-0002381 |  | Fire | BLA P 16 and ESS-0002381 | Inspection | Essential | [12 empty] | Lars | Satisfactory | Andreas | Satisfactory | NO |  | See meeting 2017-08-16 found on confluence A&S
Acoustics
|  |  | R14 |  |  | Acoustic requirements | H09 shall conform with description in General review of acoustic design, ESS-0006406 |  |  | ESS-0006406 |  | Essential | Outside Acoustics only | [10 empty] | Acoustic consultant shall review drawings during PD and in written statement, specify how acoustic constraints shall be adapted. DD: Update of statement after DD drawings are finished. | Lars | Not Answered | Andreas | Satisfactory | YES |  | Needs input from stakehoölders regarding noise production levels of their equipment
|  |  | R15 |  |  | Stack/Vent | A vent stack is required. |  |  | FS report, Platom |  | Essential | Outside Acoustics | [10 empty] | Zlatan Inert; needs to review placement and requirements in his SR Doc (Excel) | Viggo | N/A | Andreas | Satisfactory | NO
|  |  | R16 |  |  | Workplace Design | Section 18 of the Work Environment Ordinance (SFS 1977:1166). To be created in conjunction with Zlatan Idnert Acoustics advisor. |  |  | AFS 2009:2 |  | Essential | Inside Acoustics | [10 empty] | Noise and acoustics; Section 32, p 14. | Samuel | Satisfactory | Andreas | Satisfactory | NO |  | See meeting with Zlatan 2017-08-23. awaiting his report.
|  |  | R17 | 128 | H09.100.1004 | Design of pump room to control noise levels | The pump room H09.100.1004 shall be designed so that the noise level in the room, while all pumps are running, does not exceed boundary conditions according to AFS 2015:16. |  |  | BAL P 25 | Inspection | Essential | [12 empty] | Lars | Satisfactory | Andreas | N/A | NO |  | See meeting with Zlatan 2017-08-23. awaiting his report.
|  |  | R18 |  |  | Noise from ventilation stack | The ventilation stack may cause noise, if the noise from the ventilation stack is estimated to exceed current permission limits, actions shall be taken in order to reduce the noise from the ventilation stack to below these limits (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). |  |  | BLA P 28 |  | Essential | [12 empty] | Lars | N/A | Andreas | Satisfactory | No |  | See meeting with Zlatan 2017-08-23. awaiting his report.
Moisture
|  |  | R19 | 106 107 118 | H09.100.1110 H09.100.1115 H09.100.1016 | Surface treatment | All materials and all surfaces in the controlled area, (included Barrier area H09.100.1016) shall be chosen according to TBY – “Technical regulations for surface treatment” in order to ease decontamination. Floors in Changing rooms H09.100.1110, H09.100.1115 and anjent WC to these rooms shall have surfaces according TBY Exit routs from controlled area dose not require to have TBY surfaces. Minimum fire retardant compliance is defined by the Fire Strategy Report (BR01DT-TBSIGDPS--Fire Safety Strategy Report.pdf (ESS-0002381 rev. 11)). | ESS-0002381 | radiation safety | BLA P 17 | Inspection | Essential | [12 empty] | Lars | Not Answered | Andreas | Not Answered | YES |  | SEC: Is there TBY in the rooms were the waste comes from? Exit routes may become controlled area. => Tobias: No See meeting with Roger Duveskog on TBY issues 2017-08-28
|  |  | R20 |  |  | Content in concrete (RH) | Moisture content & drying time required for application of the epoxy on the concrete floor and walls RH level in the concrete. TBY (English Version). The concrete needs to dry 2-3 months before epoxy can be applied. According to meeting with Roger Duveskog 2017-08-28, the humidity in the concrete is specified in the TBY documentation for each surface and epoxy paint. |  |  |  | Analysis | Essential | [12 empty] | Lars | Not Answered | Andreas | Satisfactory | YES | CFIL-224 | SEC reports that the concrete needs to dry 2-3 months before epoxy can be applied.
Accessibility
|  |  | R21 |  |  | H09 accessibility | H09 shall be accessible according to applicable laws and regulations, with certain dispensations. There is an ESS accessibility report (CHESS ESS-0058749) | PBL BBR | Building | PBL BBR | Inspection | Essential | [10 empty] | RE.F03-34 | Accessibility consultant shall review drawings and confirm conformity in written statement. PD: After PD drawings are finished. DD: Update of statement after DD drawings are finished. Statement ESS-0036375 | Samuel | Satisfactory | Andreas | N/A | No |  | Accessibility requirements shall apply to office if it is placed outside of radiation zone. Samuel: Will be reviewd by Sofia Friberg, prel. before 22 sept.
|  |  | R22 |  |  | H09 accessibility | Chapter 8, Sections 1, 4, 7 and 9 of the Planning and Building Act (2010:900), PBA, and in Chapter 3, Sections 4, 18 and 23 of the Planning and Building Ordinance (2011:338), this may relate to the office area. |  |  | Planning and Building Act (2010:900)Planning and Building Ordinance (2011:338) | Analysis | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | Samuel: Will be reviewd by Sofia Friberg, prel. before 22 sept.
Environment
|  |  | R23 |  |  | Watertight construction | The H09 Waste Management Building shall be designed and constructed as watertight construction, meaning that water needs to be contained within its perimeter walls. (not applicable for office section) The border is the same as the controlled area, the border of the controlled area shall be shown in the layout. Please refer to TBY for guidlines and specifications. | ESS.SyR-9 |  | Technical description (ESS-0000006) | Inspection | Essential |  |  | Inspection of drawings. | [8 empty] | Where required to contain possible leakage/spill in case of emergency (1st Floor) and daily use. | Lars | Satisfactory | Andreas | Satisfactory | YES | CFRFI-332 CFIL-222 | SEC: Where is the actual boarder? Tobias: See A drawing
|  |  | R24 |  |  | Building Materials Declaration | Built in products shall be certified according to Byggvarubedömningen (BVB) and achieve the criteria levels for “Recommended” or “Accepted”. Unless functional safety demands are of higher importance |  |  | CF Plan for Sustainable Selection of Materials (ESS-0012582) | Inspection | Useful | [11 empty] | Inspection of BVB level "Accepted" or "Recommended". | Lars | Not Answered | Andreas | Satisfactory | Yes |  | For DD
|  |  | R25 |  |  | Zinc/Copper in contact with water | Materials used outdoors/indoors containing zinc/copper (e.g. galvanized steel) shall be free of these substances or coated (e.g. with paint or lacquer), if they are exposed to groundwater or high water runoffs and there is a risk of release of these substances into aquatic environments. This is an requirement on both horizontal and vertical surfaces. Therefore all steel exposed to water runoffs (i.e. steel in the floor level) needs to be stainless, but other steel parts that are more protected can be galvanized. |  |  | CF Plan for Sustainable Selection of Materials (ESS-0012582) | Inspection | Useful | [11 empty] | Inspection of BPD3 or product specification. | Lars | Not Answered | Andreas | Not Answered | Yes | CFIL-225 | S: See Jira SEC: Both Horizontal and Vertical surfaces.
|  |  | R26 | 92 - 97 110 132 106-108 122 123 |  | Sustainable forestry | Wood and wood-based products shall originate from sustainably managed forests. Applicable in the office section and externally. |  |  | CF Plan for Sustainable Selection of Materials (ESS-0012582) | Inspection | Useful | [11 empty] | Inspection of recognized forest certification schemes, such as FSC, PEFC or similar schemes; or evidence for chain of custody; or written confirmation from the supplier or other documentary evidence; and approval in ESS Part Database. | Lars | Question(s) | Andreas | N/A | No
|  |  | R27 |  |  | Halogenated materials | Materials shall be free of halogens (F, Cl, Br, I). No known exceptions to this has been done in other buildings |  |  | CF Plan for Sustainable Selection of Materials (ESS-0012582) | Inspection | Useful | [11 empty] | Inspection of BPD3 or product specification. | Lars | N/A | Andreas | N/A | No
|  |  | R28 |  |  | Sustainability | CF Sustainability requirements ESS-0031401 |  |  | ESS-0031401 | Verification | Useful | [12 empty] | Lars | Not Answered | Andreas | Not Answered | Yes
Architecture
|  |  | R138 |  |  | ESH System requirements waste building | The system requirements for the waste building found in the ESH ESS-0183700 shall be followed and commenetd on. Due to arrival date of late Dec 2018 it will de handeled in Detail Design | ESS-0183700 |  |  |  | Essential | [12 empty] | Samuel | Not Answered | Andreas | Not Answered | Yes
|  |  | R142 |  | H09.100.1001 H09.100.1003 H09.100.1004 H09.100.1008 H09.100.1009 H09.100.1019 H09.100.1020 H09.100.1021 H09.100.1022 H09.100.1023 | Forklift accessability | It shall be possible to access room H09.100.1001, 1003, 1008, 1009 1019, 1020, 1021, 1022, and 1023 with a forklift. It shall not be possible to access room H09.100.1004 with a forklift. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | Yes
|  |  | R143 |  | H09.090.1001 H09.100.1002 | Access to basement | There is a need for a stainless hatch to access room H09.090.1001 from room H09.100.1002. The size of the stainless hatch shall be approximately 1x1m2. There is also a need for a ladder of some sort to avoid the need for jumping. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  |  | R127 | 88 | H09.100.1008 | Room dimensions for Low and intermediatio storage room | The dimensions of low and intermediate storage room H09.100.1008 will be defined by the shape of the building. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R128 | 89 | H09.100.1009 | Room dimensions Overhead crane hall room | The dimensions of overhead crane hall H09.100.1009 will be defined by the shape of the building. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R29 | 89 | H09.100.1009 | Operation area of overhead Crane in room H09.100.1009 | The overhead crane in room H09.100.1009 shall be able to operate throughout the length of the overhead crane hall H09.100.1009, the design shall be made in order to allow the hook print to be as large as possible. |  | Transport | BLA P 14 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No |  | Tommy: This is too big distance
|  | Structural | R34 | 89 | H09.100.1009 | surface water runoff to sumps in overhead crane hall H09.100.1009 | The overhead crane hall H09.100.1009 shall be designed so that water (from e.g. decontamination of fire trucks, sprinkling etc.) runoff to drain sumps (in-situ), preventing water from flowing from the overhead crane hall into adjacent rooms. (no runoff shall be close to the compactor) The floor in the overhed crane hall shall be plane |  | Structure | BLA P 25 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No |  | S: It should be mentioned in the requirement that the floor still needs to be plain.
|  | Architectural | R55 | 88 | H09.100.1008 | Storage room H09.100.1008 shall be full height | The storage room for low level waste H09.100.1008 needs to be full height. |  | structure, radiation safety | BLA P 27 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Satisfactory | No
|  | Architectural | R77 | 89 | H09.100.1009 | Outer gates dimensions | Gates to the overhead crane hall H09.100.1009 shall have dimensions so that ATB12K (require W= 3.7m, H= 4.6 m) carried on a Terminalfordon, a fire truck (require W=3,7m, H=4.6m), a 30 m3 tanker truck can go throug . Also the biggest things from AD (HWL=3.5 x 3 x 10 m) shall be able to pass. see reference in ESS-0149584 | ACC.CF-1656 | Transport | BLA P 14 & 20 | Inspection | Essential | [11 empty] | PD and DD: Review drawings. Construction: inspection. | Bengt-Åke | Question(s) | Andreas | Question(s) | No |  | Data of radioactive Waste Transport Container ATB12K and applicable vehicles is found in ESS-0149584
|  | Architectural | R78 | 89 | H09.100.1009 | Placement of doors and gates | Applicable doors, gates and openings shall be placed in consideration o radiation sources, in order to minimise the dose exposure to the staff. |  | Radiation safety | BLA P 19 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No | CFIL-373
|  | Architectural | R99 | 89 | H09.100.1009 | Space for compactor in the overhead crane hall | There shall be space reserved along the side of the hall for a compactor (not in CF scope) with a footprint of approximately 5x2,15m2. The space where the compactor shall stand needs to be accessible using the overhead crane, No drain sump should be close to the area that is appointed for the compactor. |  | Structural Electrical | BLA P 24 | Analysis | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Satisfactory | No |  | Återkommer. Footprint + ryggningsavstånd + arbetsyta krävs för A. Vikt och placering krävs för S. Prisförslag etc begärt 2017-07-13 inväntar återkoppling från ATF skandinavien AB
|  | Architectural | R100 | 89 | H09.100.1009 | overhead crane clearance | The overhead crane hall H09.100.1009 shall have an overhead clearance under the overhead crane of at least 7 m, final height to be approved by ES&H. (ventilation space above to be considered) |  | structural, Transport | BLA P 25 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | No |  | SEC: Good to have margins on the height. => This information needs to be required from Transport + HVAC + fire and Electric
|  | Architectural | R73 | 89 135 | H09.100.1009 H09.115.1002 | Access to controlled HVAC H09.115.1002 135 from overhead crane hall H09.100.1009 | Access to the controlled HVAC ventilation room H09.115.1002 from the overhead crane hall H09.100.1009 shall be possible in order to enable future change fo parts of the HVAC ventilation system |  | Transport | BLA P 18 | Analysis | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | SEC: Need to be incorporated in crane detailed design.
|  | Architectural | R35 | 89 99 133 | H09.100.1009 H09.100.1019 H09.100.1001 | Prevent high dose exposure during mould transport | Measures shall be taken to prevent high dose exposure to personal transporting: o Empty moulds from outside the grouting room to the inside of the grouting room H09.100.1001. o Grouted moulds from the grouting room H09.100.1001 into the Nuclide characterisation room H09.100.1019 and back again. o Grouted moulds from the grouting room H09.100.1001 into the Mould vessel (in Overhead crane hall room H09.100.1009 for final transportation to final storage of radioactive waste (SKB) (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). | Operation | Floor plan layout | BLA P 18 | Inspection | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | No |  | Samuel: Is the current plan layout ok with regards to the issue? Tobias: Yes, 20170913
|  | Architectural | R80 | 89 90 91 125 124 |  | Controlling pressure variation (doors) | Doors and gates in the controlled area of H09 shall be self-closing and opened so that the self-closing mechanism do not have to work against the pressure difference when closing. |  | Transport | BLA P 19 | Inspection | Essential | [12 empty] | Bengt-Åke | Not Answered | Andreas | N/A | Yes |  | DD issue
|  | Architectural | R51-54 | 90 | H09.100.1023 | Space reservation for Sorting station in sorting room H09.100.1023 | The sorting station shall be shown as a dotted outline in the sorting room, dimension to be given by ES&H. Required for movable Shielded Glove Box Isolator, Shielded storage box, also space for 4 moulds and with a wall mounted robotic arm operated from a distance etc. (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2) Dimensisons supplied by ES&H final m2 to be accepted by stakeholder. There shall be space for storage and usage of movable shielding function. The shielding function shall be flexible and possible to adjust so that it can be used to isolate one or more moulds. Dimensions supplied by ES&H final m2 to be accepted by stakeholder. There shall be space for a function for waste compaction before grouting (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)) |  | Radiation safety | BLA P 27 |  | Essential | [12 empty] | Samuel | Not Answered | Andreas | N/A | Yes | CFIL-334 | Hot cell is not required according to verbal agreement with Per Persson and Tommy Hansson. A movable shielded glove box isolater is about 2.4x1.4 m Samuel: Is the current plan layout ok with regards to the issue?
|  | Architectural | R95 | 91 | H09.100.1021 | Size of decontamination room H09.100.1021 | There shall also be space reserved in the decontamination room H09.100.1021 for future equipment not provided by CF. Such as work benches, a blast-cleaner, industrial component washing machine, high-pressure washing booth, wheel blaster, dry blasting glove box, as well as a number of smaller machines, work benches and tools (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). |  |  | BLA P 22 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No | CFRFI-334
|  | Architectural | R62 | 99 | H09.100.1019 | Size of Nuclide characterisation room H09.100.1019 | In H09 there shall be a Nuclide characterisation room H09.100.1019 (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). The room shall be About 6 m long and 2.3 m in width after shielding blocks has been applied. In order to enable valid nuclide specific measurement, there shall be room for a scale that is to be placed on top of the floor, dimensions to be supplied by ES&H The room shall be accessible from both ends. And it shall be possible to enter the room with a FL 5 forklift cariying a mould with demensions 1.2x1.2x1.2 m3 |  |  | BLA P 29 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | Yes | CFRFI-304
|  | Architectural | R31 | 99 133 | H09.100.1019 H09.100.1001 | Room relations of rooms H09.100.1019 and H09.100.1001 | The Nuclide characterisation room H09.100.1019 shall be on the same floor level as the grouting room H09.100.1001 |  |  | BLA P 18 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  | Architectural | R88 | 106 107 | H09.100.1110 H09.100.1115 | Changing room design | The ESS-document “Changeroom Design, Operation and Maintenance A Nuclear Industry Code of Practice” (Changeroom Design, Operation and Maintenance A Nuclear Industry Code of Practice (ESS-0087557 rev. 1)) shall be taken into consideration when designing the changing room(s). |  | Radiation safety | BLA P 21 |  | Useful | [12 empty] | Samuel | Question(s) | Andreas | N/A | No
|  |  | R149 |  |  | Assigned HVAC space in the truss beams over the office parts | The maximum diameter that are needed to be assigned space for in the truss beams over the office part is 500 mm pipe + 100 mm insulation. This gives a total maximum diameter of 700 mm. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory |  | CFIL-232
|  | Architectural | R83 | 108 | H09.100.1016 | Barrier area H09.100.1016 shall be climate controlled (partition wall) | The Barrier area shall be a buffer between the controlled area and the uncontrolled area, and the partitioning shall be fire rated. The border between controlled and uncontrolled area is to be shown in the A drawings. |  | Fire | BLA P 20 |  | Essential | [12 empty] | Viggo | Question(s) | Andreas | N/A | No
|  | Architectural | R84 | 108 | H09.100.1016 | Barrier area storage | Area for storage of clean/dirty gowns shall be taken under consideration. |  | Radiation safety | BLA P 21 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R48 | 111 | H09.100.1003 | Reception station for LSC H09.100.1003 | The room shall be designed for docking the 5 Ton lead shielded cask to the process system, and minimise the risk for contamination in case a hose is detached during emptying procedure. It shall be possible to access the reception station via a stainless hatch /manhole from above. The hatch shall be able to take the same load as the surrounding slab. The walls shall be made in 300 mm concrete in order to reduce the background radiation. The door to the room shall consist of 2 door halves, made of 10mm thick steal and with a small overlap to block the line of sight. A reception station control panel shall be placed outside the room. |  | Radiation Safety | BLA P 26 & Waste management Plan for the ESS facility – (ESS-0004020 rev. 2 | Inspection | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes | CFIL-357 CFRFI-329 | Samuel: According to consolidated plan Tobias: Container for transport of radioactive sludge and ion-exchange resin is found in ESS-0217859. The hatch may be normally closed and to be lifted using studs that may be apply when it is needed to lift the hatch. For door dimension see R169.
|  | Architectural | R49 | 111 | H09.100.1003 | Room is required for a mobile platform in the reception station LSC H09.100.1003. | Safety of the worker shall be taken into consideration such as fall protection, protection in case of leaking connections of the LSC etc. |  | Radiation safety | BLA P 27 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes |  | ES&H to define the requirement or accept the scope of the floor hatch i.e size weight, insulation, material
|  | Architectural | R93 | 114 | H09.100.1012 | Design and size of chemical laboratory H09.100.1012 | The chemical laboratory H09.100.1012 shall be equipped with corresponding equipment, to be determined by ES&H. 2 fume tables are needed. A fume table have aproximatly 1.7x0.8m2 foot print |  |  | BLA P 22 |  | Essential | [12 empty] | Viggo | Question(s) | Andreas | N/A | Yes |  | The cemistry laboritory in Ringhals is approximately 6x8 m. It shall be space for 2 fume cupboards, a number of benches. A sink, a floor drain, eye wash and safety shower, and ventilated chemical storage lockers
|  | Architectural | R42 | 115 | H09.100.1015 | Low background radiation required in radiological laboratory H09.100.1015 | Special consideration shall be taken in order to obtain low background radiation in the radiological laboratory. This is needed in order to preform precise radiological measurements. Calculations regarding necessary radiation shielding shall be provided from ES&H. (similar to x-ray rooms in hospital) |  | Radiation safety | BLA P 26 | Inspection | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Satisfactory | No
|  | Architectural | R43 | 115 | H09.100.1015 | Radiological laboratory room design H09.100.1015 | The sizes, and future placing of objects (e.g. storage lockers, detectors, instrumentation, working stations etc.) has to be taken into consideration when designing the radiological laboratory room |  | Radiation safety | BLA P 26 | Inspection | Essential | [12 empty] | Viggo | Question(s) | Andreas | N/A | Yes
|  | Architectural | R85 | 116 | H09.100.1016 | Cleaning and pre-radiation control area exist | There shall be space for cleaning and pre-radiation control area in H09.100.1016 placed so that the workers need to pass through it on their way through the barrier area. The required distances shall be at least 10m long and 8m wide |  | Radiation safety | BLA P 21 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No | CFRFI-313
|  | Architectural | R86 | 116 | H09.100.1017 | Cleaning and pre-radiation control area storage H09.100.1017 | Storage of clean overals and shoes shall be accessable close to the Cleaning and pre-radiation control area. |  | Radiation safety | BLA P 21 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | Samuel: According to consolidated plan
|  | Architectural | R40 | 117 | H09.100.1002 | Positioning of the purification room H09.100.1002 | The purification room and the position of sources in the room shall be configured in a way that minimises radiation exposure to workers during maintenance or repair operations, Waste management Plan for the ESS facility – ESS-0004020 rev. 2. |  | Radiation safety/Floor plan | BLA P 25 & Waste management Plan for the ESS facility – (ESS-0004020 rev. 2) | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R41 | 117 | H09.100.1002 | Containment functions in the purification room H09.100.1002 | The Purification room shall have one or more confinement functions, through which any accidental spill is contained, (i.e. internal screen walls, or a process type solution) Consideration shall be taken to possible radioactive hazard in case of leakage. |  | Radiation safety | BLA P 25 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  | Architectural | R44 | 117 | H09.100.1002 | Placement of tanks in resin storage part of Purification room H09.100.1002 | The resin storage tanks might be the source of high radiation levels. In order to reduce the dose outside the walls of the Purification room, the tanks shall be located close to an outer wall as a physical protection defence barrier. |  | Radiation safety | BLA P 26 | Inspection | Essential | [12 empty] | Viggo | Question(s) | Andreas | N/A | Yes
|  | Architectural | R45 | 117 | H09.100.1002 | Exposure from radiation and resin tanks shall be minimised H09.100.1002 | The resin storage and the position of sources shall be configured in a way that minimise dose exposure to workers during maintenance or repair operations (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). It shall be ensured that workers are never exposed from more than one resin storage tank at a time (e.g. by placing the resin storage tanks inside radiation shielded functions or separate the resin storage tanks using movable radiation shielding etc.). For shielding reasons there is a need for the intermediate floor between this room and room H09.110.1003 to be at least 100 mm of concrete. |  | Radiation safety | BLA P 26 & Waste management Plan for the ESS facility – (ESS-0004020 rev. 2 | Inspection | Essential | [12 empty] | Viggo | Question(s) | Andreas | Question(s) | Yes | CFRFI-309
|  | Architectural | R32 | 117 128 129 | H09.100.1002 H09.100.1007 H09.100.1004 | Penetrations through walls between tank-, pump- and purification room | When designing the order in which the Tank room H09.100.1007, the Pump room H09.100.1004 and the Purification H09.100.1002 room the walls shall be designed to account for proper pipe penetrations through the walls (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). and reduce building costs. |  |  | BLA P 18 |  | Essential | [12 empty] | Viggo | Question(s) | Andreas | Not Answered | Yes
|  | Architectural | R30 | 117 128 129 | H09.100.1002 H09.100.1007 H09.100.1004 H09.110.1003 | relation between tank-. Pump- and purification room | The tank room H09.100.1007, the pump room H09.100.1004 and the purification rooms shall be placed close to each other in order to prevent unnecessary piping. |  |  | BLA P 18 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  | Architectural | R65 | 118 | H09.100.1004 | Position of Waste water monitoring | The waste water monitoring shall be close to where the building is conecting to the main ESS sewage system, in connection to VA-SYD. |  |  | BLA P 30 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | Yes |  | SEC: VA-syd connection or the Building connection to main sewage system? Tobias: To the main sewage system that leads to the VA-Syd connection. The funktion it is be situated in the RAD-Lab. Samuel: According to consolidated plan, samuel to check room number and position matches.
|  | Architectural | R67 | 118 | H09.100.1004 | Low RAD background required in measuring chaimber | The need for low background radiation inside the measurement chamber for waste water monitoring in the pump room, shall be taken into consideration in the design process. |  |  | BLA P 30 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | The function used to be In RAD Lab
|  |  | R139 |  |  | Radiation sheald of rad-lab | There shall be no line of sight between the rad lab H09.100.1015 and any other room where waste is processed or stored. This shall be ensured via chicane or other arrangements. The radiation shielding shall be at least 300mm. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory |  | CFRFI-314
|  | Architectural | R74 |  | H09.110.1005 | Space for storing overhead crane tools | There shall be a specially assigned space for storing tools for the overhead crane. |  | Transport | BLA P 18 | Inspection | Essential | [12 empty] | Samuel | Question(s) | Andreas | Satisfactory | No |  | Tobias: Spec specificed. In desription
|  | Architectural | R87 | 119 | H09.100.1006 H09.100.1107 | Cleaning rooms H09.100.1006 and H09.100.1107 | There needs to be one cleaning room on the controlled area H09.100.1006, and one cleaning room on the un controlled area H09.100.1107. They need to be large enouth to fit storing of cleaning equipment, a sink etc. |  | Radiation safety | BLA P 21 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | N/A | No
|  | Architectural | R98 | 125 | H09.100.1022 | Space of the hot work room H09.100.1022 | The Hot work room H09.100.1022 needs to be large enouth to fit Hot work equipment (e.g. band saw, circular saw, baling machine, in-drum compactor, blowtorcher, flame/plasma/laser-cutting, shredder, welding equipment, rescue scissors, work benches, air dehumidification & filtering). It shall be at least 39.3 m2 | (ESS-0004020 rev. 2) |  | BLA P 24 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No | CFRFI-334
|  | Fire | R38 | 128 | H09.100.1004 | Design of pump room H09.100.1004 to control fire | If possible, the pump room H09.100.1004 shall be divided into separate rooms/compartments, in consideration to minimise the effect of fire. In this case, the possibility for electrical separation shall also be taken into consideration. This will also reduce radiation exposure to the workers during service and maintenance. check with BY |  | Radiation safety | BLA P 25 | Inspection | Essential | [12 empty] | Viggo | Question(s) | Andreas | N/A | No |  | Requirement Needs to be updated has changed in context
|  | Architectural | R36 | 133 | H09.100.1001 | Grouting room H09.100.1001 | H09 shall be designed with space to solidify and store solid waste with higher radioactivity than is permitted for incineration or melting. The waste container for this purpose shall be a mould of the type that is used in Swedish final disposal system according to ESS-document “Waste Management Plan for the ESS facility” (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). References of mould types are found in the “ESS-document Acceptanskriterier för avfall till SFR” (Acceptanskriterier för avfall till SFR (ESS-0087555 rev. 1)). |  | structure & Architechture | BLA P 17 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | Samuel: According to consolidated plan
|  | Architectural | R96 | 133 | H09.100.1001 | Size of grouting room H09.100.1001 - storage | The grouting room H09.100.1001 shall be spacious enough to serve as a storage for at least 8 filled moulds each being 1.2 m2 The space (in layout version 2017-08-14) of 83.2 m2 is sufficient, |  | Radiation safety | BLA P 23 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R102 | 133 | H09.100.1001 | Penetrations to grouting room H09.100.1001 | Penetrations into the grouting room shall be sealable enabling to block radioactive aerosols, gases and dust as well as direct radiation. |  | Structure | BLA P 23 | Inspection | Essential | [12 empty] | Samuel | N/A | Andreas | Question(s) | YES |  | S: No info yet regarding the penetrations
|  | Architectural | R71 | 134 | H09.100.1026 | Roof access | It shall be possible to access the roof of the building from inside the building SEC have established contact with supplier | ESS-0051197 | environment monitoring | BLA P 16 | Analysis | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Question(s) | No | CFRFI-317 | S: Hatch dimensions not specified
|  | Architectural | R57 | 134 135 | H09.115.1001 H09.115.1002 | Ventilation shall be seperated into 2 rooms | There shall be at least two separate ventilation rooms, one in the controlled-, and one in the uncontrolled area. |  | structure, radiation safety | BLA P 28 | Analysis | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A |  | CFIL-214
|  | Architectural | R39 | 136 | H09.110.1003 | Access to second floor of purification room H09.110.1003. | in order to minimise the radiation exposure to the workers, it should be possibile to enter the second floor of the Purification room H09.110.1003, directly from stairwell and storage level 2 |  | Radiation safety | BLA P 25 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R37 | 137 | H09.110.1002 | Cement distribution shall be enabled | There shall be a way to distribute cement, concrete and cement ingredients to the grouting room from above, i.e in-situ floor/roof with penetrations for materials to run through. |  |  | BLA P 20 | Inspection | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Satisfactory | No |  | SEC: Why not buy ready conrete when needed instead? Tobias: it is a very compex and specific process. The machine is found in the Process navisworks draings.
|  | Architectural | R89 | 137 | H09.110.1002 | Radiological zoning of Cement distribution room H09.110.1002 | This cement distribution room shall be classified as conventional, uncontrolled area. |  | Radiation safety | BLA P 21 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  | Architectural | R90 | 137 | H09.110.1002 | Access too Cement distribution room H09.110.1002 | The Cement distribution room H09.110.1002 shall have a door or gate to the outside of H09 in order to enable access for workers, and loading of cement ingredients and 1000 kg bags measuring (HWD) 1100X900X1200 mm. This room is in on the uncontroled area. |  | Transport | BLA P 21 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Question(s) | No | CFIL-216 | S: Dimensions of door? Tobias: The doors shall be large enouth to allow 1,000 kg big bags to pas into the room. S: Size of bags? Tobias: Längd 1200 mm, bredd 900 mm, höjd 1100 mm. se http://www.finja.se/produkter/gjuta-mura-putsa-laga/vinterbetong-storsack
|  | Architectural | R91 | 137 | H09.110.1002 | Size of Cement distribution room H09.110.1002 - big bags | The cement distribution room H09.110.1002 shall be constructed so that it can store, distribute and handle 4+4 big bags a 1 000 kg/piece (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). The total mass in the room is specified as 14 Tons in total, concrete, calc etc. See ESS-0184371 |  | structural | BLA P 21 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Question(s) | Yes | CFRFI-324 | S: Still unclear how this loads are distributed. T: See ESS-0184371
|  | Architectural | R58 | 145 |  | Size of ventilation stack | The dimensions of the ventilation stack shall be sufficient to allow ventilation air velocity of 10 m/s. |  | structure, radiation safety | BLA P 28 |  | Essential | [12 empty] | Viggo | N/A | Andreas | Question(s) | Yes | CFIL-221 | S: Dimensions of stack given by Boris. Is it verified that this dimensions fulfil this requirement?
|  | Architectural | R59 | 145 | H09.115.1003 | Position of ventilation stack monitoring room | The ventilation stack monitoring room, needs to be on the second level of the building, and close to the ventilation stack. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  | Architectural | R60 | 145 | H09.115.1003 | Space and penetrations in the stack monitoring room H09.115.1003 | there shall be space and penetrations reserved for equipment devoted to environmental monitoring and samplings housed in this room (Environmental monitoring plan (ESS-0051197 rev.2)); |  | C&M | BLA P 29 & Environmental monitoring plan (ESS-0051197 rev.2) |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | YES | CFRFI-316 | S: Penetrations is not defined at this stage. Samuel: Who verifies the current location and size?
|  | Architectural | R69 | 129 | H09.100.1007 | Gallery Access | Waste Building to be connected to installation gallery in the target building. Process pipes with water etc shall be ariving via this gallery and end up in the Tank room H09.100.1007 |  | site infrastructure | FS resport, Platom | Inspection | Essential | [11 empty] | Some typ of connection will be required for the process water to and from the D&E buildings | Viggo | Satisfactory | Andreas | Satisfactory | No
|  |  | R47 |  | H09.100.1007 | Height of watertight walls in tank room | The concrete wall section need to be 1400 mm high to be able to contain water from largest tank (120 m3) plus 10% of remaining tanks |  |  | ESS-0012603 |  | Essential | [12 empty] | Samuel | Satisfactory |  | Satisfactory | Yes
|  |  | R129 | 90 | H09.100.1023 | Room dimensions Soorting room | The dimensions of Sorting room H09.100.1023 shall allow operational space for the functions described in R51-54. it shall be at least 76.8 m2 |  |  |  |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  |  | R64 |  | H09.100.1020 | Room dimensions maintainance workshop | maintainance workshop room shall be at least 47.9 m2 |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory |  | N/A | No
|  |  | R130 | 91 | H09.100.1021 | Room dimensions decontamination room | The dimensions of Decontamination room H09.100.1021 shall allow operational space for the functions described in R94 and R95. it shall be a minimum of 77.3 m2 |  |  |  |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  |  | R61 |  | H09.100.1052 | Room dimensions COM room | Minimum size of COM room: 3x5m |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory |  | N/A | No
|  |  | R63 |  | H09.100.1053 | Room dimensions EL room | Minimum size of EL-room: 3x5m |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory |  | N/A | No | CFIL-247
|  |  | R131 | 92 | H09.100.1069 | Room dimensions office room | The dimensions of office shal allow space for 6 full time employees (FTE). |  |  | BLA P 10 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  |  | R133 | 106 | H09.100.1061 | Room dimensions and floor of Changing room 1 | The dimensions of changing room 1 H09.100.1061 shall allow operational space for at least 6 Full Time employees and the room shall fulfill TBY requirements . |  |  |  |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  |  | R134 | 107 | H09.100.1066 | Room dimensions and floor of Changing room 2 | The dimensions of changing room 2 H09.100.1066 shall allow operational space for at least 6 Full Time Equivalents. And the the room shall fulfill TBY requirements . |  |  |  |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No
|  | Architectural | R70 |  | H09.100.1069 | Access to office | The office part of H09 shall be accessible according to norm in ESS-document “DM—RA-TBSI------Program for Accessibility within the ESS premises.docx” (ESS-0058749 rev. 1). | ESS-0058749 | Access | BLA P 17 | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | Samuel: Will be reviewd by Sofia Friberg, prel. before 22 sept.
|  |  | R72 |  |  | Architecture | H09 shall be designed according to Design Manual Accelerator Buildings / G01, G02 & G04, ESS-0013533 |  |  | ESS-0013533 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R141 |  | H09.090.1001 H09.100.1002 | Need for lifting device | It would be usefull with a lifting loop or a similar device in the HD/F slab above. |  |  |  | Analysis | Useful | [12 empty] | Samuel | Satisfactory | Andreas | Not Answered | Yes
|  | Architectural | R75 |  |  | surface treatment/finishing requirements | The floor material, selected according to TBY, is easy to decontaminate, therefore it shall also cover the lower part of the wall. How high up on the lower part of the wall the floor material shall be applied, shall be decided in consideration of the fluids, and the volume of fluids that is to be handled in the room, as well as the characters of this fluids. |  | radiation safety | BLA P 18 | Inspection | Essential | [12 empty] | Samuel | Question(s) | Andreas | Satisfactory | Yes |  | DD Level of detail agreed in PD
|  | Architectural | R76 |  | H09.100.1009 | Forklift charging station | H09 shall be equipped with charging station(s) for electrical forklift (not in CF scope). To be shown as a dotted line. |  | Fire | BLA P 18 | Inspection | Essential | [12 empty] | Viggo | Satisfactory | Andreas | N/A | No |  | S: Mounted on top of slab or moulded-in? Tobias: This is a small simple device placed on a wall.
|  | Architectural | R79 |  |  | Motor powered gates and doors | The following doors and gates in H09 shall be automated. - Gates between the overhead crane hall H09.100.1009 and the outside H09.100.1000. - Doors between the overhead crane hall H09.100.1009 and the maintainance workshop H09.100.1020. - Doors between the overhead crane hall H09.100.1009 and the soorting room H09.100.1023 - Doors between the overhead crane hall H09.100.1009 and the Nuclide caracterisation room H09.100.1019 |  | Transport | BLA P 19 | Inspection | Essential | [12 empty] | Samuel | Not Answered | Andreas | N/A | Yes
|  | Architectural | R82 |  |  | Mechanical penetration (hatches) for temporary installations | There shall be a function enabling temporary installation of cables, hoses, etc. between rooms belonging to different fire compartments, without compromising the integrity of the fire compartments; o The function is to be used when special temporary installations (e.g. temporary power, tubing or instrument cabling for monitoring etc.) between fire compartments are needed. o The function shall be placed next to each doors/openings, and in respect to other functions in both rooms as well as the risk for internal flooding and the risk of direct radiation. o The function shall not affect the function of the door, or how it may be used. |  | Fire | BLA P 20 | Inspection | Essential | [12 empty] | Samuel | Not Answered | Andreas | Not Answered | Yes |  | DD
Radiation safety
[7 empty] | This category has not been clearley defined by the stakeholders ES&H awaiting input . |  |  | ? |  | Essential | [16 empty] | Yes
Structure
|  | Structural | R103 |  |  | Expansion joints | Need to be watertight, if needed |  |  |  |  | Essential | [12 empty] | Viggo | N/A | Andreas | Satisfactory | No
|  |  | R94 |  | H09.100.1007 | tank casings | The tanks shall be placed on tank casings, raising the tanks from the floor above the level of water that are expected in case the largest tank and additionally 10% of all the other tanks would break. NOT part of CF scope |  |  |  |  | Essential | [12 empty] | Samuel | N/A |  | Satisfactory | Yes
|  | Structural | R115 | 88 | H09.100.1008 | Floor of LLW & ILW storage H09.100.1008 needs to be strong | The floor of the storage room H09.100.1008 for waste shall be constructed so that it will support future mobile radiation shielding blocks made of concrete. |  | structure, radiation safety | BLA P 27 |  | Essential | [12 empty] | Viggo | N/A | Andreas | Satisfactory | No
|  | Structural | R113 | 89 | H09.100.1009 | Floor load in overhead crane hall | The floor of the overhead crane hall shall be able to carry the weight of a ATB 12K loaded with moulds as well as a vehicle loaded with a ATB 12K loaded with moulds. Data is fouind in ESS-0149584 |  | Transport | BLA P 25 | Inspection | Essential | [12 empty] | Viggo | N/A | Andreas | Satisfactory | No | CFRFI-320 | Radioactive Waste Transport Container ATB12K and applicable vehicles are found in ESS-0149584. Basis for the load plan is found in ESS-0184371
|  |  | R137 |  |  | Loads on floors and intermediate floors | Requirements on loads on level 100, 110 and 115 are All is documented in ESS-0184371 | R115 |  | ESS-0184371 |  | Essential | [12 empty] | Samuel | N/A | Andreas | Satisfactory | No
|  | Structural | R106 | 89 | H09.100.1009 | Overhead Crane foundation | The structure shall support a 20,000 kg capacity crane, to be defined by transport expert. |  | Transport | BLA P 14 |  | Essential | [12 empty] | Viggo | N/A | Andreas | Question(s) | Yes |  | S: New crane definition needed, due to changed span width
|  |  | R132 |  | H09.100.1002 | embankment of ion resin tanks | According to ESS-0012603, there is a need for containment of the ion resin tanks contents. Each tank, found in ESS-0150431 and ESS-0150432, have a volume of 5 m3. The containment measures need to hold a volume of the largest tank + 10% of the volume of the remaining tanks. In this case, it summs up to a total of 5.5 m3. |  |  | ESS-0012603 |  | Essential | Vital | [11 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  | Structural | R116 | 99 |  | Function to regulate distance between the colimator and the specimen | The function (not part of CF scope) to regulate the distance between the collimator and the specimen, might need to be moulded into the floor and therefore has to be taken into consideration when designing the Nuclide Characterisation Room. |  |  | BLA P 29 |  | Essential | [12 empty] | Samuel | N/A | Andreas | Not Answered | Yes |  | DD
|  | Structural | R104 | 133 | H09.100.1001 H09.100.1002 | Walls in High Radiocative areas | Grouting room (H09.100.1001) will be built with thicker upstands in preparation for shielding blocks NOT IN CF SCOPE along the outer walls to prevent high dose rates outside of the building. The purification room (H09.100.1002) will be built with upstands for shielding blocks NOT IN CF SCOPE towards the outer wall as well as upstands for shielding blocks NOT IN CF SCOPE for chicanes shall be provided. | Project report -V1-100915. p 11, 5. | site infrastructure | Platom Report # 1147351-2 |  | Essential | [11 empty] | The building will provide shielding to specific romms/areas only. To be advised at a later date. | Viggo | Question(s) | Andreas | Satisfactory | Yes |  | S: Upstands are in CF scope S: Suggesting 300mm exterior walls casted in-situ, then add movable concrete blocks of sufficient thickness on the inside. Ok? S: Maybe this should be mentioned in the requirement, that it is ok to build with normal walls, and then add moveable blocks that is not part of the structure? Tobias: is this more clear?
|  | Structural | R111 | 133 | H09.100.1001 | Background reduction from grouting room H09.100.1001 | The suspended slab of the grouting room H09.100.1001 shall be designed so that the prescribed maximum dose levels to above spaces are not exceeded (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). However, the thicknes is reccomended by ES&H to be 100mm |  | radiation safety | BLA P 23 | Inspection | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes |  | S: Holes need to be defined, size and location Tobias: As we are not planing to do any thick in-situ sheilding blocks, this may be a require we should considre to abandon. Samuel: Issue status unclear and impact in PD for A. Tobas: Detail sufficient for PD
|  | Structural | R110 | 137 | H09.110.1002 | Lifting capacity of telfer lift in Cementation room H09.110.1002 | The overhead clearance of the cement distribution room shall be sufficient to allow a function to move substance from the bags into the concrete mix function (Waste management Plan for the ESS facility – (ESS-0004020 rev. 2)). (maintainance access needs to be considered) |  | Transport | BLA P 21 |  | Essential | [12 empty] | Viggo | Satisfactory | Andreas | Not Answered | Yes |  | S: Telfer needs to be defined. Tobias: Telfer is defined, all Transport documentation is found in the Transport confluence page for H09 S: This documentation is only for hook print
|  | Structural | R114 | 145 |  | Wall thickness of ventilation stack | The wall thickness of the ventilation stack shall be dimensioned according to ”SS-EN 1993-2:2006; Eurokod 3 Dimensionering av stålkonstruktioner Del 3-2: Skorstenar” and ”Svenska Stålbyggnadsnormer N1-N4”. ATT: Structural Design not in this scope completed by stack supplier. |  |  | BLA P 28 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Satisfactory | Yes | CFIL-215 | Samuel: Can we attain a simplified summary from HVAC or other issue owner? Awaiting answer.
|  | Structural | R105 |  |  | Containment and personal safety | Walls, doors and walkways shall, where applicable, be protected against collision from forklift or truck (using e.g. guard barriers, guard rails, bollards etc.). |  | Radiation safety and personal safety | BLA P 17 | Inspection | Essential | [12 empty] | Lars | Question(s) | Andreas | Question(s) | Yes |  | S: Needs to be defined in architectural drawings. A: This is done later in the DD.
|  | Structural | R107 |  |  | Structure Risk analysis is needed | The structure shall be equipped with well proven robust safety functions defined based on risk analysis. Shown in basis of design. A basis for risk analysis is found in ESS-0183699. |  | Radiation safety | BLA P 16 |  | Essential | [12 empty] | Samuel | N/A | Andreas | Question(s) | Yes |  | Samuel: Detail level in PD unclear and has who will perform the risk analysis? A DD issue? S: We refer to DD for risk analysis (CC3)
|  | Structural | R109 |  |  | Wall dimensions for shielding purposes | Certain walls of H09 shall contribute to the shielding functions with 300mm thickness and upstands. The shielding level shall be sufficient to assure that the dose rate outside H09, due to radioactive waste inside H09, are kept under a boundary as specified in the ESS-document “General Safety Objectives” (General Safety Objectives (ESS-0000004 rev. 5)). Calculations regarding necessary radiation shielding shall be provided from ES&H. | ESS-0000004 | Structure | BLA P 17 | Inspection | Essential | [12 empty] | Lars | Question(s) | Andreas | Satisfactory | Yes
|  |  | R32 |  |  | Roof slab dimensions for shielding purposes | A roof slab made of normal HDF is enough to provide sufficient radiation shielding. |  |  |  | Inspection | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No | CFRFI-308
|  | Structural | R112 |  |  | Space for fire rated penetrations for pipes and cabling | Fire compartmentation of the building is fitted with fire rated penetrations for pipes and cabling. The fire rated penetrations shall provide space for all functions in the room (including foreseen functions that is not included in the CF scope), the fire rated penetrations shall also have an extra capacity of at least 20%. The reason for this is that future functions may be required from the regulatory body. |  | Fire | BLA P 16 | Inspection | Essential | [12 empty] | Samuel | N/A | Andreas | Not Answered | Yes |  | S: Holes need to be defined, size and location Tobias: May this wait untill DD? I would like you to see some inside Barsebäck if possible Samuel: DD
|  |  | R117 |  |  | Floor settlement | H09 shall keep the differential floor settlement to within guidlines specified by HUS AMA | ACC.CF-1609 |  |  |  | Essential | [11 empty] | FS and PD: Review drawings. Construction: measurments | Lars | Question(s) | Andreas | Satisfactory | No
|  |  | R135 |  |  | design for columns distance | 6.5 m free space between columns would be nice, cc ca 7 m, as this would be good for the container size. |  |  |  | Measurment | Useful | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No | CFIL-228 | meeting notes 2017-08-30
|  |  | R118 |  |  | Seismic Requiremnts | N/A |  |  |  |  | Essential | [11 empty] | Status to be checed by Building Owner att handover of PD to DD | Lars | N/A | Andreas | Question(s) | No | CFRFI-321 | S: Can we be sure that that it won't be raised any seismic requirements? (e.g. due to SSM). Maybe it's better to highlight this for DD, it has a very large impact on the structures.
|  |  | R119 |  |  | loads from overhead cranes | The loads of overhead cranes are to be specified by transport system owners. |  |  |  |  | Essential | [12 empty] | Lars | N/A | Andreas | Question(s) | YES | CFRFI-330 | S: All cranes need to be defined in DD, as early as possible.
|  |  | R136 | 109 | H09.110.1007 H09.100.1020 H09.100.1021 H09.100.1023 | Overhead crane in room H09.110.1007, H09.100.1020, H09.100.1021 and H09.100.1023 | Functions in rooms H09.110.1007, H09.100.1020, H09.100.1021 and H09.100.1023 require a 6 T overhead crane. |  |  |  |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes |  | S: Should be put in R120
|  |  | R63 |  | H09.100.1004 | Radiation safety | The room shall be prepeared with curtain wall's that provide radiation sheilding functions between each pump. Possition and hight shall be according to specifications from process and made in DD. |  |  |  |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes
|  |  | R140 |  | H09.100.1012 | Explosions in chem lab | According to ESS-0183699 explosions are to be expected in the laboratory. The consequences of such a explosion needs to be mitigated. |  |  | ESS-0183699 |  | Essential | [12 empty] | Samuel | Not Answered | Andreas | Not Answered | Yes
Investigate
|  |  | R144 |  | H09.110.1001 H09.110.1005 H09.110.1007 | Access to level 110 and fall protection. | It shall be possible to directly via fixed ladder from level 100 have access to rooms H09.110.1001, H09.110.1005 and H09.110.1007. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | DD
|  |  | R145 |  | H09.090.1000 H09.090.1002 | Door between culvert and stair | The door between the culvert and the stair only a escape route, only to be opened in case of emergency. |  |  | ESS-0183699 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R146 |  | H09.090.1000 H09.090.1002 | TBY in Culvert | TBY shall be applied in the entire culvert. Both the blue and the green parts. |  |  | ESS-0183699 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | N/A | Yes
|  |  | R147 |  |  | Metalic plates in situ for ATB 12K | There ATB 12K shall always be placed on the same spot on metallic plates in situ in order to save the epoxy floor and enable optimal conditions for loading etc To be done in DD. Data of ATB 12K is found in ESS-0149584 |  |  | ESS-0155076 |  | Useful | [12 empty] | Samuel | N/A | Andreas | Question(s) | Yes
|  |  | R148 |  | H09.090.1001 | Epoxi on floor and basement walls | The floor and the walls of the room shall be watertight at least to a level corresponding to a tank rapture of 100% of the largest tank, +10% of all the other tanks in the room. |  |  | ESS-0012603 |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | N/A | Yes
|  |  | R151 |  | H09.090.1000 H09.090.1002 H09.100.1007 | Additional space for pipe penetrations. | Additional space should be reserved in the process pipe penetrations throug walls for future piping via the culvert. To be done in DD. |  |  | ESS-0155076 |  | Desirable | [12 empty] | Samuel | Question(s) | Andreas | N/A | Yes
|  |  | R152 |  | H09.100.1007 H09.100.1009 | Interlock slush door function | There is a need for an interlock slush function between room H09.100.1007 and H09.100.1009 to enable access between the rooms. The slush function shall consist of a water tight 1.5m high wall inside the tank room. There shall be a 1.5m high self-closing door in the 1.5m high wall with an opening with of 1.4m, that opens towards the tank room, so that, in event of tank rapture, the water pressure will push to close and seal the door. It shall be possible to exit the room by an emergency escape ladder/staircase of some sort over the 1.5m high wall in case of an evacuation event. The 1.5m high wall shall cover at least the whole with of the entrance door between H09.100.1009 and H09.100.1007, ensuring that water do not exit the tank room H09.100.1007. The distance between the wall of the room and the 1.5m wall shall be 1m. The position of the tanks shall be taken into consideration when selecting the position of the door between H09.100.1007 and H09.100.1007 as well as the self-closing door and the emergency escape ladder/staircase in the 1.5m wall. |  |  | ESS-0181792 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  |  | R153 |  |  | Correlation with HVAC documentation | The drawings shall be correlated withthe HVAC document ESS-0185517 |  |  | ESS-0185517 ESS-0190272 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  |  | R154 |  | H09.100.1003 | Slope in H09.100.1003 floor | The floor in RRS H09.100.1003 shall have a slope towards the channel drain in the floor. |  |  | ESS-0181792 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Question(s) | Yes |  | Slope in concrete or surface material?
|  |  | R155 |  | H09.115.1001 | Door from uncontrolled HVAC to overhead crane hall. | This door opening shall have free opening dimensions of at least 1.8m wide, and 2.1m high. There shall also be a threshold under the door, stopping internal flooding to enter H09.100.1009 in case of fire extinguish water should be used in H09.115.1001 |  |  | ESS-0185517 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Question(s) | Yes |  | Threshhold in concrete?
|  |  | R156 |  | H09.100.1024 | Size of boiler process room | The boiler process room shall have 4.5m in height and be 20m2 large in order to host the tritium boiler. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Question(s) | Yes
|  |  | R162 |  |  | Security strategy | The ESS Security strategy found in ESS-0050211, shall be followed. This will be implemented on classes of doors, windows etc. |  |  | ESS-0050211 |  | Essential | [12 empty] | Lars | Question(s) | Andreas | Question(s) | Yes
|  |  | R163 |  | H09.090.1001 | Volume of basement | The basement shall be equipped with tanks, pumps, shielding and pipes. The total volume of the room exclusive these objects shall have a volume that are able to contain a volume of 100m3 residual fire water. |  |  | ESS-0002381 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R167 |  | H09.100.1009 H09.100.1001 H09.100.1003 H09.100.1004 H09.100.1007 H09.100.1020 H09.100.1023 | Door sizes | The doors free opening between the overhead crane hall H09.100.1009 and the following rooms shall be 2m wide, and 2.8m high: Grouting room H09.100.1001, RRS room H09.100.1003, Tank room H09.100.1007, Maintenance workshop H09.100.1020, Sorting room H09.100.1023. The door between the overhead crane hall H09.100.1009 and the Nuclide characterisation room shall be 3,9m high and 3.5m wide. The door between the overhead crane hall H09.100.1009 and the pump room H09.100.1004 shall be 2m high 1.2 m wide. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | Satisfactory | No
|  |  | R168 |  |  | Door sealing | To enable for the ventilation system to withhold the under pressure, it is important that specific doors (specified by HVAC) are equipped with sealing strips around the whole door frame. Sealing strips shall be made of Silicone Rubber, EPDM, Nitrile or Neoprene rubber where the joint / seal is slightly protected. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | Yes
|  |  | R169 |  |  | Fire rated doors | Doors in borders between fire compartments shall be fire rated |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | Yes
|  |  | R170 |  | H09.115.1001 H09.115.1002 | emergency door between controlled and uncontrolled HVAC | There shall be a emergency exit door between H09.115.1001 and H09.115.1002. There shall be a threshold to the door stopping fire extinguish water to flow between the two rooms. |  |  | ESS-0185517 |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R172 |  | H09.115.1002 | Door from controlled HVAC to overhead crane hall. | There shall be a way to transport larger HVAC-components between H09.115.1002 and the outside of H90. This may be made via a door in the wall to H09.100.1009. The door opening shall have free inlet dimensions of at least 1.8m wide, and 2.1m high. |  |  |  |  | Essential | [12 empty] | Lars | Satisfactory | Andreas | N/A | No
|  |  | R173 |  | H09.100.1011 | Room H09.100.1011 | The room H09.100.1011 shall be at least 8m2, and there shall not be any line of sight between the inside of room H09.100.1011 and the overhead crane hall H09.100.1009. The wall thickness between any point inside of room H09.100.1011 and any point inside of room H09.100.1009 shall be at least 300mm. The door to H09.100.1011 may not be in a wall between the rooms H09.100.1011 and H09.100.1009, nether in a wall facing H09.100.1008. |  |  |  |  | Essential | [12 empty] | Samuel | Question(s) | Andreas | Question(s) | Yes
|  |  | R174 |  | H09.110.1003 | Space reservation for legal sampling station | Space shall be reserved for the legal sampling station, requiring 1.5x1.5m2 floor surface. The reserved space shall be positioned along the wall and on top of the pump room. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
|  |  | R175 |  | H09.100.1055 | Space requirement entrance room | The entrance room shall be at least 2 m wide, and 2.9 m long. It shall have one door to enter and one to exit the room. |  |  |  |  | Essential | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No |  | The dimensions makes it posible to make a future installation of a circlelock system.
|  |  | R176 |  | H09.100.1009 H09.100.1010 | Door between corridor and overhead crane hall | The door shall open out towards the overhead crane hall (in order to keep the underpreassure on the right side of the door when opening the outer gates) and be equipped with a window that enable the user to see if someone is standing outside so that this person are not hurt by the opening of the door. |  |  |  |  | Desirable | [12 empty] | Samuel | Satisfactory | Andreas | N/A | No
Note on A1: Unique identifier
Note on B1: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on G1: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on H1: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on I1: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID. The child req. is more detailed and specific, it satisfies parts of or the entire parent req. It is also used to link requirements for validation purposes.
Note on J1: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on K1: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on L1: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on M1: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on N1: When the requirement is derived from a risk analysis. The related Risk Id shall be included.
Note on O1: Name of the last reviewer
Note on P1: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on Q1: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on R1: The expected minimum value for the parameter of interest
Note on S1: The expected nominal value for the parameter of interest
Note on T1: The expected maximum value for the parameter of interest
Note on U1: S.I. units for the value of interest specification.
Note on V1: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on W1: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on X1: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on Y1: Text describing how this requirement shall be verified. Details of how and at when verification activities should be performed. Can be a CHESS reference to Verification Plan.

## Data
Architectural resource | Initials | Source box
Lars Lindahl | Lars | LL,SM,VT, BJ
Samuel Martin | Samuel
Viggo Thormark Fröst | Viggo
Bengt-Åke Jarnestad | Bengt-Åke
Structural resource | Iinitals | Source box
Henrik Norén | Henrik | HN,AA,TC
Anderas Abrahamsson | Andreas
Tomas Cervin | Tomas
Possible review resoult | Short | Source box
Not applicable | N/A
Now Questions | Satisfactory
Not Answered
Questions | Question(s)
Discipline | Priority
Acoustics | Essential | 1. Essential requirements that must be included in the system
Architectural | Useful | 2. Useful capabilities that would reduce system effectiveness if left out
Availability | Desirable | 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Control&Monitoring
HVAC
ELV
Fire
Moisture
Production
Security
Structural
Transport
Verification method
Inspection
Measurment
Demonstration
Analysis
Old Room no. & name | New Room no. & name
133 grouting
117 purification
111 LSC
129 Tank room
118 Water monitoring
119 Cleaning room
88 Waste Storage
89 overhead crane hall
90 sorting room
91 Decontamination room
125 Hot works room
124 Workshop
99 nuclide caracterisation
98 Water sample room
114 Chemistry room
113 Materials storage
112 Chemicals storage
115 Radiological laboratory
106 F changingroom
107 M changingroom
108 barrier area
110 hallway
126 Shaft
127 HVAC water etc
120 COM
121 EL
122 WC
123 Coats
37

## Example
Requirement attributes. Help can be obtained by hovering with the mouse over any of the titles of the columns | [18 empty] | These are not requirement attributes.
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Comments
|  | Waste room area | The CUB waste room shall have a minimum area of 9 m² in in order to facilitate handling of waste in connection with the CUB |  |  | ESS-0013188 MoM CUB Meeting 20 | Measurement | Useful | [9 empty] | In work | A02-002 | Measurements of waste room in drawings and at commissioning
|  | Ventilation air flow | The Ventilation in all CUB rooms shall have a minimum air flow of 0,35 l/s /m2 in order to fulfill regulations |  |  | SS-EN1717 | Measurement | Essential | [9 empty] | In work |  | Measurements according to verification plan ESS-0023456
|  | Comply with SS-EN 61936-1 | The High voltage power System shall comply with SS-EN 61936-1 (standards for Power installations exceeding 1 kV) | Si-SyR123 |  | ESS-0012345 | Inspection | Essential | [9 empty] | Approved | PowerRe-14 | Verification of derived requirements (PowerRe-25, PowerRe-27, PowerRe-30)
|  | Climatic and environmental conditions humidity | The H06 indoor climate shall have average value of the relative humidity, measured over a period of 24 h of maximum 95 % in order to minimize the risk of condensation. | PowerRe-14 |  | SS-EN 61936-1 Chapter 4.4.2.1e | Inspection | Essential | [9 empty] | In review | PowerRe-25 | Verification of H06 HVAC req. derived from this req.
ESS …
XXXX
Note on A2: Unique identifier
Note on B2: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on C2: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on D2: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on E2: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID It is also used to link requirements for validation purposes.
Note on F2: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on G2: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on H2: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on I2: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on J2: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on K2: Name of the last reviewer
Note on L2: When the requirement is specific to an operating mode for the So I, the name of the mode shall be specified
Note on M2: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N2: The expected minimum value for the parameter of interest
Note on O2: The expected nominal value for the parameter of interest
Note on P2: The expected maximum value for the parameter of interest
Note on Q2: S.I. units for the value of interest specification.
Note on R2: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on S2: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on T2: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on U2: Text describing how this requirement shall be verified. Can be a CHESS reference to Verification Plan.
Note on D5: This high level requirement is broken down to several system specific requirements
Note on E6: This cell contains a reference to the ID of the parent requirement

## Req. Descript.
Requirement description's template for all types of requirements except interface requirements:
The | [System – who/what does the action]
shall | [Function – what happens e.g. store, update, send data]
the | [System – what is acted upon]
to the | [System – where the output is sent recipient or end state]
At/with | [Performance - frequency and/or quality characteristic]
when | [Event – causes of action; data receipt/user interaction]
unless/even if | [Constraint – business rule or limiting factor]
So that | [Rationale - description of value or benefit is achieved].
Example
The PUMP shall MOVE the COOLENT to the HEAT EXCHANGER at a rate of 500 LITERS PER MINUTE when THE COOLENT TEMPERATURE IS OVER 120C unless THE TEMPERATURE IS OVER 130C WHEN THE RATE WILL BE 600 LITERS PER MINUTE so that HOT COOLENT IS TAKEN AWAY FROM THE TARGET. NB! this example is all inclusive of the template above. Requirement descriptions may or may not be so extensive.
Interface requirement description form (these requirement types are written in pairs):
Your requirement
[System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface].
Your counterparts requirement
[System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].

## Revision history (hidden)
ESS-0002908 SEMP v1.5 | ESS-0002908 SEMP v1.5 | ID | Category | Name | Text |  |  | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX-YYY Interface requirements table view | Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX.SyR-TEMPLATE table view | Object Identifier | Category | Req short test | Req Text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
| New categories |  | Requirement Categories |  |  | "Derived from" is used for linking to requirement on level above | "Allocated to" is used to allocate requirements to next lower SOI (system of Interest) |  | Verification methods | Priority values, used to | [9 empty] | Status values, with "in revision" removed
Functional
| Constraint |  | Functional | [5 empty] | Inspection | Essential | [9 empty] | In work
| Environment |  | Constraint | [5 empty] | Measurement | Useful | [9 empty] | In review
| Radiation safety |  | Interface | [5 empty] | Demonstration | Desirable | [9 empty] | Approved
| Conventional safety |  | Environment | [5 empty] | Analysis | [10 empty] | Released
|  |  | Radiation safety | [16 empty] | Obsolete
| Removed categories |  | Conventional safety
Electrical
Regulatory
Operational
Mainatnance
Structural
Safety
Interface
The attribute "version" is removed in .v5 the only differance to the communicated .v4 at the SE meeting 28 dec 2014. Version was added by mistake…
Several attributes changes i .v6. The attributes marked yellow and that exist in SEMP is only renamed. 3 new attributes is added. "Object heading" to facilitate chapter struction within a DOORS 9.x module. 2 new attributes "Satisfies" and "Satisfy by" to facilitate validation linking and allocation on next level. The value attributes marked orange, is change from "real" to "string" to support scientific format. Changes is proposed 2 Feb 2015 to simpfy requirement export, import and mangement in "Excel" format only. Other document style is not supported by this template. This template will provide a unified import, internal and export format.
Changes in v.7: #1 The attribute Category have a reduced number of categories: Proposed new set is Functional; Constraints; Environment; Radiation Safety; Conventional safety; Removed is Electrical; Regulatory; Operational; Maintanance; Structural; Safety; Interface. #2 The attribute "Satisfies" is exchanged to "derived from". "Satisfy" by is replaced by "Allocated to", which is added to simplify allocation to next level and used for verifying "derived from links" In revision is removed from the Status attribute
Changes in v.8: #1 Value "Interface" added in the attribute Category. Interface was omitted by mistake in v.7 #2 The attribut "Responsible" is removed
Changes in v.9 #1 The attribute "req id" is replaced by "Object Identifier"red color above. Rationale is that only DOORS generated ID shall be used as unique requirement ID. MagicDraw generated IDs will not be used in DOORS for new added requirements in the future. #2 Minor editorial changes in revision history tab and cell A2 ands B2 with references to DOORS module is removed in the DOORS Req. format tab not to be mistaken for a attribute.
Note on C1: Unique identifier
Note on D1: • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on E1: Name of the parameter defining the performance
Note on F1: Textual description of the requirement
Note on I1: Trace to a source document, DMS Id shall be mentioned.
Note on J1: Specification of one of the fourth possible verification method
Note on K1: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on L1: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on M1: Name of the last reviewer
Note on N1: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on O1: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on P1: The expected minimum value for the parameter of interest
Note on Q1: The expected nominal value for the parameter of interest
Note on R1: The expected maximum value for the parameter of interest
Note on S1: S.I. units for the value of interest specification.
Note on T1: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on U1: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on G2: A relation attribute to relate this requirement on PBS level n to a requirement on PBS level n-1 which it satisfy. It is use to link requirements for validation purposes.
Note on H2: A relation attribute to relate this requirement on level n to the next system node that satify this requirement on PBS level n+1. It is used for allocation purposes.
Note on P2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on Q2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on R2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS