## DOORS Req. format
Requirement attributes. Help can be obtained by hovering with the mouse over any of the titles of the columns | [18 empty] | These are not requirement attributes and will not be imported into DOORS
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Comments
|  | Waste Water Accelerator | 3 m3/year of Radioactive Waste Water will be generated by Accelerator and has to be handled in H09. |  | 11500 | ESS-0092262 | Measurement | Essential | [9 empty] | In review
|  | Ion Exchange Resin Accelerator | 100 l/year of radioactive Ion Exchange Resin will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0092262 | Measurement | Essential | [9 empty] | In review
|  | Solid Waste Accelerator | 11500 kg/year of radioactive Solid Waste will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0092262 | Measurement | Essential | [9 empty] | In review
|  | Waste Water NSS | 3630 m3/year of Radioactive Waste Water will be generated by Accelerator and has to be handled in H09. |  |  | ESS-0020758 | Measurement | Essential | [9 empty] | In review
|  | Ion Exchange Resin NSS | 100 l/year of radioactive Ion Exchange Resin will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0020758 | Measurement | Essential | [9 empty] | In review
|  | Solid Waste NSS | 23500 kg/year of radioactive Solid Waste will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0020758 | Measurement | Essential | [9 empty] | In review
|  | Waste Water Target | 77 m3/year of Radioactive Waste Water will be generated by Accelerator and has to be handled in H09. |  |  | ESS-0048270 | Measurement | Essential | [9 empty] | In review
|  | Ion Exchange Resin Target | 850 l/year of radioactive Ion Exchange Resin will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0048270 | Measurement | Essential | [9 empty] | In review
|  | Solid Waste Target | 538,9kg/year of radioactive Solid Waste will be generated by Accelerator and has to be handled in H09 |  |  | ESS-0048270 | Measurement | Essential | [9 empty] | In review
|  | Waste Water H09 | 100 m3/year of Radioactive Waste Water will be generated by Accelerator and has to be handled in H09. |  |  | H09 Project | Measurement | Essential | [9 empty] | In review
|  | Ion Exchange Resin H09 | 100 l/year of radioactive Ion Exchange Resin will be generated by Accelerator and has to be handled in H09 |  |  | H09 Project | Measurement | Essential | [9 empty] | In review
|  | Solid Waste H09 | 100 kg/year of radioactive Solid Waste will be generated by Accelerator and has to be handled in H09 |  |  | H09 Project | Measurement | Essential | [9 empty] | In review
|  | Radioactive Fire Water | 425 m3/year of Radioactive Fire Water can be generated by Sprinkler activation and has to be handled in H09. |  |  | ESS-0002381 | Measurement | Essential | [9 empty] | In review
|  | Extinguishing water collection | Extinguishing water shall be collected in a special tank system and as a final measure go with the storm water to the detention ponds. The ponds shall then be shut off for sampling, treatment or disposal. | 13867 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-6
|  | Collection systems for solid and liquid waste | SI shall be equipped with collection systems with seperate fractions for solid and liquid wastes. | 13868 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-7
|  | Effective circulation pumps | All circulation pumps shall have EEI 0.23 or better | EHS-NRG-004 | ESS-0078440/ ESS-0043151 | ESS-0078440/ ESS-0043151 ESS-0031406 | Measurement | Essential | [9 empty] | In review | SRH09-8
|  | Effective electrical motors | Electrical motors shall be of energy efficiency class IE4 or better according to SS-EN 60034-30-1 | EHS-NRG-008 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | Measurement | Essential | [9 empty] | In review | SRH09-9
|  | Zinc in contact with water | Zinc in materials and products at ESS that are in contact with water and where there is a risk of release of this substance into the environment shall be replaced by other alternative materials. | EHS-SUS-002 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | Inspection | Essential | [9 empty] | In review | SRH09-16
|  | Copper in contact with water | Copper in materials and products at ESS that are in contact with water and where there is a risk of release of this substance into the environment shall be replaced by other alternative materials. | EHS-SUS-003 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | Inspection | Essential | [9 empty] | In review | SRH09-17
|  | Sulfur hexafluoride | Sulfur hexafluoride (SF6) shall not be used at ESS. | EHS-SUS-004 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | Inspection | Essential | [9 empty] | In review | SRH09-18
|  | Environmental court verdict | Chemical products shall be handled in a way that spills and leaks can not reach sewers or the environment | EHS-SUS-033 |  | ESS-0078440/ ESS-0043151 ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-24
|  | Environmental court verdict | Hazardous waste shall be handled in a way that spills and leaks can not reach sewers or the environment | EHS-SUS-038 |  | ESS-0078440/ ESS-0043151 ESS-0031402 | Inspection | Essential | [9 empty] | In review | SRH09-25
|  | Environmental court verdict | Storage of Chemical products shall take place on a surface that is impermeable for the products stored | EHS-SUS-043 |  | ESS-0078440/ ESS-0043151 ESS-0031403 | Inspection | Essential | [9 empty] | In review | SRH09-26
|  | Environmental court verdict | Storage of chemical products shall be fitted with bunding or similar to protect against leaks | EHS-SUS-048 |  | ESS-0078440/ ESS-0043151 ESS-0031404 | Inspection | Essential | [9 empty] | In review | SRH09-27
|  | Environmental court verdict | Storage of chemical products shall be otherwise designed so that precipitation does not accumulate in it | EHS-SUS-053 |  | ESS-0078440/ ESS-0043151 ESS-0031405 | Inspection | Essential | [9 empty] | In review | SRH09-28
|  | Environmental court verdict | The volyme of the bunding to collect spill in the chemical storage shall correspond to the volyme of the largest container in the storage plus 10% of the total volyme of the other stored chemical containers | EHS-SUS-058 |  | ESS-0078440/ ESS-0043151 ESS-0031406 | Inspection | Essential | [9 empty] | In review | SRH09-29
|  | Environmental court verdict | Storage of hazardous waste shall take place on a surface that is impermeable for the waste stored | EHS-SUS-063 |  | ESS-0078440/ ESS-0043151 ESS-0031407 | Inspection | Essential | [9 empty] | In review | SRH09-30
|  | Environmental court verdict | Storage of hazardous watse shall be fitted with bunding or similar to protect against leaks | EHS-SUS-068 |  | ESS-0078440/ ESS-0043151 ESS-0031408 | Inspection | Essential | [9 empty] | In review | SRH09-31
|  | Environmental court verdict | Storage of hazardous waste shall be otherwise designed so that precipitation does not accumulate in it | EHS-SUS-073 |  | ESS-0078440/ ESS-0043151 ESS-0031409 | Inspection | Essential | [9 empty] | In review | SRH09-32
|  | Environmental court verdict | The volyme of the bunding to collect spill in the hazardous waste storage shall correspond to the volyme of the largest container in the storage plus 10% of the total volyme of the other stored chemical containers | EHS-SUS-078 |  | ESS-0078440/ ESS-0043151 ESS-0031410 | Inspection | Essential | [9 empty] | In review | SRH09-33
|  | Environmental court verdict | Storage tanks shall be equipped with overfill protection | EHS-SUS-083 |  | ESS-0078440/ ESS-0043151 ESS-0031411 | Inspection | Essential | [9 empty] | In review | SRH09-34
|  | Environmental court verdict | Absorbent shall be available at chemical storages | EHS-SUS-088 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-35
|  | Environmental court verdict | Absorbent shall be available at hazardous waste storages | EHS-SUS-093 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-36
|  | Volume of wastewater from laboratories | Waste water from laboratories shall be minimized and collected locally for monitoring of contamination level prior to discharge to the municipal sewage system. | 13842 |  | ESS-0031412 | Inspection | Essential | [9 empty] | In review | SRH09-37
|  | Chemical waste | Chemical waste from laboratories shall be stored adjacent to where it was generated, awaiting disposal. | 13844 |  | ESS-0031412 | Inspection | Essential | [9 empty] | In review | SRH09-38
|  | Environmental court verdict approve sewage effluents | Diverted effluents to the municipal sewage system has to be approved in advance by the municipality and by the supervicory authorities according to the Swedish environmental code | EHS-SUS-122 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-42
|  | Environmental court verdict close flow to municipas sewage | It shall be possible to close the flow to the municipal sewage system. | EHS-SUS-132 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-44
|  | Environmental court verdict collect sewage | Sewage, where discharge is prohibited, shall be collected and handled as waste | EHS-SUS-133 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-45
|  | Monitoring of contamination level | The volume of wastewater from laboratories shall be minimized and collected locally for monitoring of contamination level prior to discharge to the municipal sewage system. | 13851 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-46
|  | Laboratories design | Laboratories shall be designed so as to prevent hazardous substances from ending up in the wastewater. | 13852 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-47
|  | Floor drains | Floor drains shall be connected to separate tanks if drains are needed in potentially (radioactive) contaminated areas. | 13853 |  | CF sustain req ESS-0031401 | Inspection | Essential | [9 empty] | In review | SRH09-48
|  | Engineering design | All facilities shall be designed to avoid formation of explosive athmospheres, in order to avoid explosion hazards. Possible design strategies include 1) choice of non flammables OR 2) flammables kept with 75% margin to Lower Explosion Limit or Fire point OR 3) inert atmosphere AND/OR 4) get in compliance with the explosions requirements EHS-EXP-XXX | EHS-EXP-005 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-108
|  | Engineering alignment standard | Explosion hazards shall be reduced by design in alignment with ISO-CEN-SIS standards. | EHS-EXP-011 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-109
|  | Program flammable liquids | Handling of flammable liquids shall be in compliance with SÄIFS2000:2, SRVFS2005:10, MSBFS2014:5, MSBFS2014:1 (aerosols), | EHS-EXP-067 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-122
|  | Program flammable gas | Handling of flammable gas shall be in compliance with SÄIFS1998:7 & SÄIFS2004:4 & SÄIFS1998:7 | EHS-EXP-073 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-123
|  | Program comply with act | Handling of flammable gas and liquids shall be in compliance with Flammable and Explosive Act SFS2010:1011 & the ordinance SFS2010:1075 & the regulation SRVF 2004:7, MSBFS2010:4, SÄIFS 1994:5, AFS1995:5, AFS2003:3, MSBFS2013:3 | EHS-EXP-079 |  | ESS-0078440/ ESS-0043151 | Inspection | Essential | [9 empty] | In review | SRH09-124
Note on A2: Unique identifier
Note on B2: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on C2: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on D2: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on E2: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID. The child req. is more detailed and specific, it satisfies parts of or the entire parent req. It is also used to link requirements for validation purposes.
Note on F2: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on G2: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on H2: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on I2: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on J2: When the requirement is derived from a risk analysis. The related Risk Id shall be included.
Note on K2: Name of the last reviewer
Note on L2: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on M2: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N2: The expected minimum value for the parameter of interest
Note on O2: The expected nominal value for the parameter of interest
Note on P2: The expected maximum value for the parameter of interest
Note on Q2: S.I. units for the value of interest specification.
Note on R2: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on S2: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on T2: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on U2: Text describing how this requirement shall be verified. Details of how and at when verification activities should be performed. Can be a CHESS reference to Verification Plan.

## Example
Requirement attributes. Help can be obtained by hovering with the mouse over any of the titles of the columns | [18 empty] | These are not requirement attributes.
Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status | User Defined ID | Verification Description | Comments
|  | Waste room area | The CUB waste room shall have a minimum area of 9 m² in in order to facilitate handling of waste in connection with the CUB |  |  | ESS-0013188 MoM CUB Meeting 20 | Measurement | Useful | [9 empty] | In work | A02-002 | Measurements of waste room in drawings and at commissioning
|  | Ventilation air flow | The Ventilation in all CUB rooms shall have a minimum air flow of 0,35 l/s /m2 in order to fulfill regulations |  |  | SS-EN1717 | Measurement | Essential | [9 empty] | In work |  | Measurements according to verification plan ESS-0023456
|  | Comply with SS-EN 61936-1 | The High voltage power System shall comply with SS-EN 61936-1 (standards for Power installations exceeding 1 kV) | Si-SyR123 |  | ESS-0012345 | Inspection | Essential | [9 empty] | Approved | PowerRe-14 | Verification of derived requirements (PowerRe-25, PowerRe-27, PowerRe-30)
|  | Climatic and environmental conditions humidity | The H06 indoor climate shall have average value of the relative humidity, measured over a period of 24 h of maximum 95 % in order to minimize the risk of condensation. | PowerRe-14 |  | SS-EN 61936-1 Chapter 4.4.2.1e | Inspection | Essential | [9 empty] | In review | PowerRe-25 | Verification of H06 HVAC req. derived from this req.
ESS …
XXXX
Note on A2: Unique identifier
Note on B2: Requirement categories • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on C2: A unique name or short description of requirement that identify the main topic of the requirement. Ideally 3-4 words. If it is not a unique name you can include a number at the end.
Note on D2: Textual description of the requirement This is the text of the requirement. The text shall identify: 1. The part of the system that performs the action 2. the action to be performed 3. The part of the system acted upon 4. Where the result of the action is sent/received 5. When the actions is performed and/or when the action is not performed 6. The rationale - the reason or benefit achieved (optional) See also Req. Description tab in this document. Interface req form: [System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface]. [System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].
Note on E2: If this requirement is broken down from another requirement this attribute is used to link them together. The cell should contain the ID of the parent requirement, either a User Defined ID or the Doors ID It is also used to link requirements for validation purposes.
Note on F2: A relation attribute to relate this requirement on level n to the next system node that satisfy this requirement on PBS level n+1. It is used for allocation purposes.
Note on G2: References to reports, standards, documents, emails, discussions that explain the origin of the requirement. CHESS Id shall be mentioned.
Note on H2: What's the main strategy to verify the requirement Specification of one of the four possible verification method: 1. Inspection - of drawings, items, test reports etc.. 2. Demonstration - of the action where there is no performance criteria 3. Measurement - of the action where there is a performance criteria 4. Analysis - where none of the above is appropriate e.g. certain cases related to safety or risk
Note on I2: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on J2: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on K2: Name of the last reviewer
Note on L2: When the requirement is specific to an operating mode for the So I, the name of the mode shall be specified
Note on M2: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on N2: The expected minimum value for the parameter of interest
Note on O2: The expected nominal value for the parameter of interest
Note on P2: The expected maximum value for the parameter of interest
Note on Q2: S.I. units for the value of interest specification.
Note on R2: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on S2: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on T2: This is a string of text needed in order to track changes and to link requirements together. You can allocate a number; note that DOORS will allocate its own requirement ID once the requirement is imported into doors.
Note on U2: Text describing how this requirement shall be verified. Can be a CHESS reference to Verification Plan.
Note on D5: This high level requirement is broken down to several system specific requirements
Note on E6: This cell contains a reference to the ID of the parent requirement

## Req. Descript.
Requirement description's template for all types of requirements except interface requirements:
The | [System – who/what does the action]
shall | [Function – what happens e.g. store, update, send data]
the | [System – what is acted upon]
to the | [System – where the output is sent recipient or end state]
At/with | [Performance - frequency and/or quality characteristic]
when | [Event – causes of action; data receipt/user interaction]
unless/even if | [Constraint – business rule or limiting factor]
So that | [Rationale - description of value or benefit is achieved].
Example
The PUMP shall MOVE the COOLENT to the HEAT EXCHANGER at a rate of 500 LITERS PER MINUTE when THE COOLENT TEMPERATURE IS OVER 120C unless THE TEMPERATURE IS OVER 130C WHEN THE RATE WILL BE 600 LITERS PER MINUTE so that HOT COOLENT IS TAKEN AWAY FROM THE TARGET. NB! this example is all inclusive of the template above. Requirement descriptions may or may not be so extensive.
Interface requirement description form (these requirement types are written in pairs):
Your requirement
[System 1] shall [interact] with [System 2] [as defined in or having the characteristics shown in] [the document that defines the interface].
Your counterparts requirement
[System 2] shall [interact] with [System 1] [as defined in or having the characteristics shown in] [the document that defines the interface].

## Revision history (hidden)
ESS-0002908 SEMP v1.5 | ESS-0002908 SEMP v1.5 | ID | Category | Name | Text |  |  | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX-YYY Interface requirements table view | Object Identifier | Category | Req short text | Req text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
DOORS temp module | XXX.SyR-TEMPLATE table view | Object Identifier | Category | Req short test | Req Text | Derived from | Allocated to | Source | Verification Method | Priority | Related risk | Reviewed by | Operating Mode | State | Min value | Nominal value | Max value | Unit | Condition | Status
| New categories |  | Requirement Categories |  |  | "Derived from" is used for linking to requirement on level above | "Allocated to" is used to allocate requirements to next lower SOI (system of Interest) |  | Verification methods | Priority values, used to | [9 empty] | Status values, with "in revision" removed
Functional
| Constraint |  | Functional | [5 empty] | Inspection | Essential | [9 empty] | In work
| Environment |  | Constraint | [5 empty] | Measurement | Useful | [9 empty] | In review
| Radiation safety |  | Interface | [5 empty] | Demonstration | Desirable | [9 empty] | Approved
| Conventional safety |  | Environment | [5 empty] | Analysis | [10 empty] | Released
|  |  | Radiation safety | [16 empty] | Obsolete
| Removed categories |  | Conventional safety
Electrical
Regulatory
Operational
Mainatnance
Structural
Safety
Interface
The attribute "version" is removed in .v5 the only differance to the communicated .v4 at the SE meeting 28 dec 2014. Version was added by mistake…
Several attributes changes i .v6. The attributes marked yellow and that exist in SEMP is only renamed. 3 new attributes is added. "Object heading" to facilitate chapter struction within a DOORS 9.x module. 2 new attributes "Satisfies" and "Satisfy by" to facilitate validation linking and allocation on next level. The value attributes marked orange, is change from "real" to "string" to support scientific format. Changes is proposed 2 Feb 2015 to simpfy requirement export, import and mangement in "Excel" format only. Other document style is not supported by this template. This template will provide a unified import, internal and export format.
Changes in v.7: #1 The attribute Category have a reduced number of categories: Proposed new set is Functional; Constraints; Environment; Radiation Safety; Conventional safety; Removed is Electrical; Regulatory; Operational; Maintanance; Structural; Safety; Interface. #2 The attribute "Satisfies" is exchanged to "derived from". "Satisfy" by is replaced by "Allocated to", which is added to simplify allocation to next level and used for verifying "derived from links" In revision is removed from the Status attribute
Changes in v.8: #1 Value "Interface" added in the attribute Category. Interface was omitted by mistake in v.7 #2 The attribut "Responsible" is removed
Changes in v.9 #1 The attribute "req id" is replaced by "Object Identifier"red color above. Rationale is that only DOORS generated ID shall be used as unique requirement ID. MagicDraw generated IDs will not be used in DOORS for new added requirements in the future. #2 Minor editorial changes in revision history tab and cell A2 ands B2 with references to DOORS module is removed in the DOORS Req. format tab not to be mistaken for a attribute.
Note on C1: Unique identifier
Note on D1: • Functional • Constraint • Environment • Interface • Radiation safety • Conventional safety
Note on E1: Name of the parameter defining the performance
Note on F1: Textual description of the requirement
Note on I1: Trace to a source document, DMS Id shall be mentioned.
Note on J1: Specification of one of the fourth possible verification method
Note on K1: 3 levels: 1. Essential requirements that must be included in the system 2. Useful capabilities that would reduce system effectiveness if left out 3. Desirable capabilities that make the system more desirable to certain stakeholders.
Note on L1: When the requirement is derived from a risk analysis. The related risk Id shall be mentioned.
Note on M1: Name of the last reviewer
Note on N1: When the requirement is specific to an operating mode for the SoI, the name of the mode shall be specified
Note on O1: When the requirement is specific to an ESS state, the name of the state shall be specified
Note on P1: The expected minimum value for the parameter of interest
Note on Q1: The expected nominal value for the parameter of interest
Note on R1: The expected maximum value for the parameter of interest
Note on S1: S.I. units for the value of interest specification.
Note on T1: ‹When the performance is specific to certain conditions (normal or off-normal), the condition is described (e.g. limited time, for a specific context)
Note on U1: • In Work, • In review, • Approved, • In revision, • Released, • Obsolete.
Note on G2: A relation attribute to relate this requirement on PBS level n to a requirement on PBS level n-1 which it satisfy. It is use to link requirements for validation purposes.
Note on H2: A relation attribute to relate this requirement on level n to the next system node that satify this requirement on PBS level n+1. It is used for allocation purposes.
Note on P2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on Q2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS
Note on R2: Value represented as string instead of a "real" to extend DOORS value range to support scientific format. Any format transformation from string to …… shall be done outside DOORS